# VOLUME II – A - Part 2

# Civil and Water Supply

# Technical Specification

Contents

| Description | Page no. |
| --- | --- |
| VOLUME II – A - Section - 2 |  |
| Sub section C1: Technical specification for excavation and filling | 5-12 |
| Sub section C3: Technical specification for cast-in-situ concrete and allied works | 15-46 |
| Sub section C4: Technical specifications for masonry and allied works | 49-58 |
| Sub section C5: Technical specification for plastering and allied works | 61-65 |
| Sub section WS1: Technical specifications for laying of pipes and fittings /specials | 83-95 |
| Sub section WS3: Technical specifications for laying and jointing of ductile iron pipes and fittings | 98-107 |
| Sub section WS4: Technical specifications for HDPE pipes and UPVC pipes | 110-125 |
| Sub section WS5: Technical specifications for valves | 128-140 |
| Sub section WS7: Technical specifications for ductile iron pipes | 143-162 |
| ANNEXURES |  |
| Annexure B - Frequency of sampling and testing |  |
| Annexure C – List of tender drawings |  |
| Annexure D - Geotechnical investigation report |  |
| Annexure E - EHS plan |  |
| Annexure F - Tolerance and acceptance criteria |  |
| Annexure G - List of manufacturers and dealers |  |
| Annexure H - Quality Assurance Violation Clauses |  |
| Annexure I - Supplier and contractor code of conduct |  |
| Annexure J - Energy & Environment Conservation Measures |  |
| Annexure K - Basic Rate Approval |  |
| Annexure L - Standard for onsite workers housing quarters |  |

Sub-Section - C1

Technical specification for excavation and

filling

Sub-Section - C1

Technical specification for excavation and filling

Contents

Clause no.  		Description 							Page nos.

- Scope

- General requirements

- Codes and standards

- Excavation

- Filling

- Sampling testing and quality control

Section - 	C1: Technical specification for excavation and filling

- Scope

  - This section of the specification covers the technical requirements for excavation and filling for industrial plots in & around structures, buildings, pipes, foundations, trenches, pits, drains, channels, cable ducts, underground facilities & similar works. It also covers filling areas and plinths with selected materials, conveyance and disposal of surplus soils and/or stacking them properly as directed by the Engineer.

  - The contractor shall be fully responsible for getting necessary permission from government authorities to excavate soil from the sources mentioned in the tender and should pay necessary seignerage charges to government authorities as per rules.

  - The Contractor shall be fully responsible for proper setting out of works, profiling in excavation, stacking, etc., taking adequate safety measures etc. The Contractor shall carry out all works meant within the intent of this specification even if not explicitly mentioned herein. All work shall be executed to the satisfaction of the Engineer.

  - Existing trees, shrubs, any other plants, pole lines, fences, signs, monuments, buildings, pipelines, drains, sewers, or other surface or subsurface systems/drains/facilities within or adjacent to the works being carried out which are not to be disturbed, shall be protected from damage by the Contractor shall provide and install suitable safeguards approved by the Engineer for this purpose.

  - During excavation, the Contractor shall take all necessary precautions against soil erosion, water & environmental pollution and where required to undertake additional works to achieve this objective. Before start of operations, the Contractor shall submit to the Engineer for approval, his work plan and the procedure he intends to follow for disposal of waste materials etc. and the schedule for carrying out temporary and permanent control works. However, the approval of the Engineer to such plans and procedures shall not absolve the Contractor of his responsibility for safe and sound work.

- General requirements

  - The Contractor shall make his own surveying arrangements for locating the coordinates and positions of all work and establishing the reduced levels (RL’s) at these locations based on two reference grid lines and one benchmark which will be furnished by the Owner. The Contractor has to provide at site all the required survey instruments, along with qualified surveyors, to the satisfaction of the Engineer so that the work can be carried out accurately and according to the specification and drawings.

  - The Contractor shall furnish all skilled and unskilled labour, plant, tools, tackle, equipment, men, materials required for complete execution of the work in accordance with the drawings and as described herein and/or as directed by the Engineer.

  - The Contractor shall control the grade in the vicinity of all excavations so that the surface of the ground will be properly sloped or dyed to prevent surface water from running into the excavated areas during construction.

  - All materials obtained from excavation shall remain owner’s property.  All salvaged materials of archeological importance or of value (in the opinion of the Engineer) shall be segregated from the other materials and both stacked separately and in regular manner at locations indicated by the Engineer.

  - Excavation shall include removal of trees including roots & organic remains, vegetation, grass, bushes, shrubs, plants, poles, fences, etc. that are in the area to be excavated as well as beyond the excavation line so as to ensure safety of the excavated side slopes, and of men and equipment operating in the area. Before start of excavation work, joint measurements of ground level shall be taken after cleaning all grass, vegetation, etc.

  - Excavation shall include the removal of all materials required to execute the work properly and shall be made with sufficient clearance as decided by the Engineer to permit the placing and setting of forms, inspection and completion of all works to the satisfaction of the Engineer for which the excavation was done.

  - Wherever reference is made to ‘drawings’ in this specification it shall mean the latest issue of the approved drawings.

- Codes and standards

  - All standards, specifications, acts, and codes of practice referred to herein shall be the latest editions including all applicable official amendments and revisions.

  - In case of conflict between this specification and those (IS standards, codes etc.) referred to herein (in para 3.3) the former shall prevail.

  - Some of the relevant Indian standards, Acts and Codes are referred to here below:

IS:383 	Specification for coarse and fine aggregates from natural sources for concrete.

IS:2720 (Part-II, IV to VIII, 	Methods of tests for soils - determination of water

XIV, XXI, XXIII, XXIV content etc.

XXVII to XXIX, XL)

IS:3764:  	Safety code for excavation work

IS:4081: 	Safety code for blasting and related drilling operations

IS:4701:  	Code of Practice for earth work on canals

IS:9759: 	Guidelines for Dewatering during construction.

IS:10379:	Code of practice for field control of moisture and compaction of soils for embankment and subgrade.

IS:3812	Pulverised fuel ash – specification part 2 for use as admixture in cement mortar and concrete

- Excavation

  - Excavation in all types of soils, soft and disintegrated rock (ordinary rock), and hard rock shall be done up to the required level. Excavation shall also include breaking of existing concrete RCC, Masonry work, tar and bitumen surfaces, and paving works etc. In case blasting is required the same shall be subject to the approval of Engineer. Sides and bottoms of excavation shall be cut sharp and true to line and level. Undercutting shall not be permitted. When machines are used for excavation, the last 300 mm before reaching the required level shall be excavated manually or by such equipment that soil at the required final level will be left in its natural condition.  Suitability of strata (at the bottom of excavations) for laying the foundation thereon shall be determined by the Engineer.

  - Excavation for foundations shall be to the bottom of lean concrete and as shown on drawings or as directed by the Engineer. The bottom of all excavations shall be trimmed to required levels and when excavation is carried below such levels, by error, it shall be brought back to specified level by filling with concrete of nominal mix 1:3:6/1:4:8 (cement & Fly ash (20% replacement ratio of cement with fly ash): coarse sand: 20mm down aggregates) as directed by the Engineer.

  - The Contractor shall ascertain for himself the nature of materials to be excavated and the difficulties, if any, likely to be encountered in executing this work. Cofferdams, Sheeting, shoring, bracing, maintaining suitable slopes, draining etc. shall be provided and installed by the Contractor, to the satisfaction of the Engineer.

  - All excavation for installation of underground facilities, such as piping, sewer lines, drain lines, etc. shall be open cuts. For deep and huge excavations and in other excavations, if required by the Engineer, the Contractor shall submit for Engineer’s approval (as already mentioned under Clause 1.5) an “Excavation scheme” showing the methodology to be adopted for excavation in order to maintain the stability of side slopes, means for ensuring safety of existing facilities nearby, dewatering as required etc. However, the Contractor shall be fully responsible for the scheme irrespective of any approvals granted. Benching shall be provided for deeper excavation wherever required.

  - When excavation requires bracing, sheeting or shoring etc., the Contractor shall submit drawings to the Engineer, showing arrangements and details of proposed installation. The Contractor shall also furnish all supporting calculations as called for and shall not proceed until he has received written approval from the Engineer. However, the responsibility for adequacy of such bracing, sheeting, shoring etc. will rest with the Contractor, irrespective of any approval of the Engineer.  All precautions shall be taken while excavations near existing structures are to be carried out till the backfilling is completed.

  - The Contractor shall have to constantly pump out any water collected in excavated pits and other areas due to rainwater, ground water, springs etc. and maintain dry working conditions at all times until the excavation, placement of reinforcement, shuttering, concreting, backfilling is completed. The Contractor shall remove all slush/muck from the excavated areas to keep the work area dry. Sludge pumps, if required, shall be employed by the Contractor for this purpose.

  - The Contractor shall remove all materials arising from excavations from the vicinity of the work either for direct filling, stacking and subsequent filling or for ultimate disposal as directed by the Engineer. In no case shall the excavated soil be stacked within a distance of 1.5m from the edge of excavation or one third the depth of excavation whichever is more. Material to be used for filling shall be kept separately as directed by the Engineer.

- Filling

  - Materials

- Materials to be used for filling purposes shall be stone, sand or other inorganic materials and they shall be clean and free from shingle, salts, organic, large roots and excessive amount of sod. Lumps concrete or any other foreign substances which could harm or impair the strength of the substructure in any manner.  All clods shall be suitably broken to small pieces.  When the material is mostly rock boulders, these shall be broken into pieces not larger than 150mm size.  Sand used for filling shall be clean, medium grained and free from impurities.  Fines less than 5 microns shall not be more than 20%.  In any case, the materials to be used for filling purposes shall have the prior written approval of the Engineer.

- If excavated materials are to be used for filling, then the Contractor shall select the materials from the stockpile, load and transport this material and execute the filling.  This shall include excavation of earth which may become hard due to laying in stack yard for a long period of time.

- In case the materials have to be brought from pits/quarries, then it shall be the Contractor’s responsibility for identification of such quarry areas, obtaining approval for their use from concerned authorities, excavation/quarrying, loading and carriage of such material, unloading and filling at specified locations. The Contractor shall pay any fees, royalties etc. that may have to be paid for utilization of borrow areas.

  - Filling procedure

- After completion of foundation, footings, walls and other construction below the elevation of the final grades, and prior to filling, all temporary shoring, timber, etc. shall be sequentially removed and the excavation cleaned of all trash, debris and perishable materials. Filling shall begin only with the written approval of the Engineer. Also, areas identified for filling shall be cleared of all soft pockets, vegetation, bushes, slush etc. In case of plinth and similar filling the ground shall be dressed and consolidated by ramming and light rolling.

- Fill materials shall not be dropped directly upon or against any structure or facility where there is danger of displacement or damage.  Filling shall be started after the concrete/masonry has fully set and shall be carried out in such manner so as not to cause any undue lateral thrust on any part of the structure.

- All space between foundation (concrete or masonry) and the sides of excavation shall be filled to the original surface after making allowance for settlement. Fill shall be placed in horizontal layers not exceeding 200mm loose thickness. Each layer shall be watered and compacted with proper moisture content and with such equipment as may be required to obtain a compaction/density as specified. Trucks or heavy equipment for depositing or compacting fill shall not be used within 1.5 metres of building walls, piers or other facilities which may be damaged by their weight or operations. The methods of compaction shall be subject to the approval of the Engineer. Pushing of earth for filling shall not be adopted under any circumstances.

- Fill adjacent to pipes shall be free of stones, concrete, etc. and shall be hand placed and compacted uniformly on both sides of the pipe and where practicable up to a minimum depth of 300mm over the top of pipes. While tamping around the pipes, care should be taken to avoid unequal pressure.

- Filling shall be accurately finished to line, slope, cross section and grade as shown on the drawings. Finished surface shall be free of irregularities and depressions and shall be within 20mm of the specified level.

- Where filling with stone from excavated materials is required, as per design and functional requirements, it shall be from broken pieces of boulders. At first a 75mm thick cushion of selected earth shall be laid over which the 200mm thick graded stones shall be laid in loose layers of 200mm and then the interstices filled with properly graded fine materials consisting of selected earth brought from borrow areas. Each layer shall be watered and compacted to the required density as per design and functional requirements before the next layer is laid. However, no cushion shall be required where filling is over non-rocky surface.

- Where clean stone fill is required as per design and functional requirements shall consist of clean selected stone metal of 40mm nominal size. It shall be laid in layers not exceeding 150mm (loose) and lightly tamped before the next layers laid. No compaction shall be required for this type of stone filling.

  - Compaction

- Where compaction of 90% Standard Proctor Density is called for, such compaction shall be by mechanical means but the contractor may be permitted to adopt manual means only if the Engineer finds that the desired compaction is achievable in the field.

- Where compaction to 95% Standard Proctor Density is called for, it shall be by mechanical means only.  Where access is possible, compaction shall be 12 tonne rollers smooth wheeled, sheep foot or wobbly wheeled and directed by the Engineer. A smaller weight roller may be permitted by the Engineer in special cases, but in any case, not less than 10 passes of the roller will be accepted for each layer. Each layer shall be wetted or the material dried by aeration to a moisture content of 3-5% above the Optimum Moisture Content to be determined by Contractor. Each layer shall be watered, rammed and compacted to the density as specified in the Schedule of Quantities.

- For compacting each sand layer, water shall be sprayed over it to flood it and it shall be kept flooded for 24 hours to ensure maximum compaction. Vibrocompactors shall also be used if necessary to obtain the required degree of compaction. Any temporary works required to contain sand under flooded condition shall also be undertaken.  The surface of the consolidated sand shall be dressed to required levels or slope.

- After the compacted fill has reached the desired level, the surface shall be flooded with water for 24 hours, allowed to dry and then rammed and consolidated to avoid any settlement, at a later date. The compacted surface shall be properly shaped, trimmed and consolidated to an even gradient or level. All soft spots shall be excavated, filled and consolidated.

- The degree of compaction of compacted fill in place will be subject to tests in accordance with relevant Indian Standards as desired by the Engineer. As the work progress, the Contractor shall provide the necessary facilities to make such tests. If any test indicates that the compaction achieved is less than the required as per design and functional requirements degree of compaction, the Engineer may require all fill placed subsequent to the last successfully test to be removed and re-compacted by the Contractor. Compaction procedure shall be amended as necessary to obtain satisfactory results.

- When semi-compacted fill is required as per design and functional requirements by the Engineer, the Contractor shall fill up such areas with available earth from stock piles or borrow pits or directly from excavation without special compaction except that obtained by moving trucks, etc.

- Sampling testing and quality control

  - General

- The Contractor shall carry out all sampling and testing in accordance with the relevant Indian Standards and/or International Standards and shall conduct such tests as are called for by the Engineer. Where no specific testing procedure is mentioned, the tests shall be carried out as per the prevalent accepted engineering practice to the directions of the Engineer. Tests shall be done in the field and at a laboratory approved by the Engineer and the Contractor shall submit to the Engineer, the test results in triplicate within three days after completion of a test. The Engineer may, at his discretion, waive some of the stipulations given below, for small and unimportant operations.

- Work found unsuitable for acceptance shall be removed and replaced by the Contractor. The work shall be redone as per specification requirement and to the satisfaction of the Engineer.

- Only as a very special case and that too in non-critical areas, the Engineer may accept filling work which is marginally unacceptable as per the criteria laid down. For such accepted work, payment shall be made at a reduced rate prorate to the compaction obtained against that stipulated.

  - Quality assurance programme

The Contractor shall submit and finalize a detailed field Quality Assurance Programme within 30 days from the date of award of the Contract according to the requirements of the specification. This shall include setting up of a testing laboratory, arrangement of testing apparatus/equipment, deployment of qualified/experienced manpower, preparation of format for record, Field Quality Plan, etc.  On finalized field quality plan, the owner shall identify customer hold prints beyond which work shall not proceed without written approval from the Engineer.

  - Frequency of sampling and testing including the methods for conducting the tests are given in Annexure B. The testing frequencies set forth are the desirable minimum and the Engineer shall have the full authority to carry out or call for tests as frequently as he may deem necessary to satisfy himself that the materials and works comply with the appropriate specifications.

  - Acceptance criteria

Following acceptance criteria shall be followed.

- All individual samples collected and tested should pass without any deviation when only one set of samples is tested.

- For re-test of any sample two additional samples shall be collected and tested, and both should pass without any deviation.

- Where a large number of samples are tested for a particular test than 9 samples out of every 10 consecutive samples tested shall meet the specification requirement.

- Tolerance on finished levels for important filling areas at approved intervals shall be + 20 mm.  However, for an unimportant area, tolerance up to + 57 mm shall be acceptable at the discretion of the Engineer.  However, these tolerances shall be applicable for localized areas only.

For any other references regarding permissible deviations shall be referred to the tolerance limit enclosed Annexure F.

Sub-Section - C3

Technical specification for cast-in-situ

concrete and allied works

Sub-Section - C3

Technical specification for cast-in-situ concrete and allied works

Contents

Clause no.                          Description                                                             Page   nos.

Section 1- Common requirement

1                 Scope

2                 General

3                 Codes and standards

4                 Sampling, testing and quality assurance

Section 2 - Cast-in-situ concrete

5                 Scope

6                 General requirement

7                 Materials

8                 Water

9                 Grades of concrete

10               Sampling, testing and quality assurance including construction tolerances

Section 3 - Reinforcement

11                     Scope

12                General requirements

13                Materials

14                Bending and placing

15                Cover to reinforcement

16            Sampling, testing and quality assurance

Section - C3: Technical specification for cast-in-situ concrete

and allied works

Section 1 - Common requirement

- Scope

  - The work shall include providing of materials, all necessary plant and equipment, providing adequate engineering supervision and technical personnel, skilled and unskilled labour, etc. as required to carry out the entire work as indicated on the drawings and/or described herein subsequently and/or as directed by the Engineer.

  - The Contractor shall carry out all works meant within the intent of this specification even if not explicitly mentioned herein. All works shall be executed to the satisfaction of the Engineer.

  - This specification is divided into 13 sections. The Section – 1 deals with common requirements and the other 12 sections deal with specifications for 12 different items/activities. The stipulations contained in Section-1, ‘Common Requirements’ shall form a part of the specifications of 12 different items/activities described in section2 to 13.

All these eight sections are as follows:

Section - 1 Common requirement

Section - 2 Cast-in-Situ Concrete

Section - 3 Reinforcement

Section - 4 Formwork and staging

Section - 5 Embedded parts

- General

  - Any approval, instructions, permission, checking, review, etc. whatsoever by the Engineer, shall not relieve the Contractor of his responsibility and obligation regarding adequacy, correctness, completeness, safety strength, quality, workmanship, etc.

  - The Contractor shall make his own surveying arrangements for locating the coordinates and positions of all work and establishing the reduced levels (RLs) at these locations, based on two reference grid lines and one bench mark, which will be furnished by the Owner.  The Contractor has to provide at site, faction of the Engineer so that the work can be carried out accurately and according to the specifications and drawings.

- Codes and standards

  - All applicable standards, specifications, etc. and codes of practice shall generally be the latest editions, including all applicable official amendments and revisions.  A complete set of all these documents shall generally be available at site, with the Contractor.

  - All work shall be carried out as per the stipulations contained in various sections of these specifications and the latest Indian Standards, Acts, Codes and best practices.

  - In case of conflict between the stipulations contained in various sections of these specifications and stipulations of Indian Standards, Codes, etc. the requirements of stipulations contained in various sections of these specifications, shall prevail over that of Indian Standards, Codes, etc.

  - Some of the applicable Indian Standards, Codes, etc. are referred to here below:

IS:73 	Specification for paving bitumen

IS:2062	Specification for structural steel

IS:269 	Specification for Ordinary Portland cement, 33 grade.

IS:280	Specification of mild steel wire for general engineering purposes

IS:383	Specification for coarse and fine aggregates from natural sources for concrete.

IS:432	Specification for mild steel and medium tensile steel (parts I & II) bars and hard drawn steel wire for concrete reinforcement.

IS:455 	Specification for Portland slag cement

IS:456 	 Code of practice for plain and reinforced concrete.

IS:457	Code of general construction of plain & reinforced concrete for dams & other massive structures.

IS:516 	Method of test for strength of concrete

IS:650 	Specification for standard sand for testing of cement

IS:702	Specification for industrial bitumen

IS:816	 Code of practice for use of metal arc welding for general construction in mild steel.

IS:1199	Method of sampling and analysis of concrete

IS:1200	Method of measurement of building (part-II and civil engineering works, V, VIII, XVIII)

IS:1367	Technical supply conditions for threaded steel fasteners

IS:1489	Specification for Portland-pozzolana cement

(Part-I)	Fly ash based

(Part-II)	Calcined clay based

IS:1566	Specification for Hard-drawn steel wire fabric for concrete

IS:1609	Code of practice for laying damp proof treatment using bitumen felts.

IS:1786	Specification for high strength deformed steel bars and wires for concrete reinforcement.

IS:1791	General requirements for batch type concrete mixers.

IS:1838(Part 1) Specification for preformed fillers for expansion joints in concrete pavements and structures (non extruding and resilient type).

IS:2204	Code of practice for construction of reinforced concrete shell roof.

IS:2210	Criteria for the design of reinforced concrete shell structures and folded plates.

IS:2386	Methods of test of aggregates for (Parts concrete I to VIII).

IS:2438	Specification for roller pan mixer.

IS:2502	Code of practice for bending and fixing of bares for concrete reinforcement.

IS:2505	General requirements for concrete vibrators, immersion type.

IS:2506	General requirements for concrete vibrators, screed board type.

IS:2514	Specification for concrete vibrating tables.

IS:2571	Code of practice for laying in-situ cement-concrete flooring.

IS:2645	Specification for Integral cement water proofing compounds.

IS:2722	Specification for portable swing weigh batchers for concrete. (Single and double bucket type)

IS:2750 	Specification for Steel scaffoldings

IS:2751 	Code of practice for welding of mild steel plain and deformed bars for reinforced concrete structures.

IS:3025 	Methods of sampling and test waste water.

IS:3067 	Code of practice for general design details and preparatory work for damp proofing & water proofing of buildings.

IS:3150 	Specification for hexagonal wire netting for general purposes.

IS:3366 	Specification for Pan vibrators.

IS:3370 	Code of practice for concrete (Part I structures for the storage of to IV) liquids.)

IS:3384 	Specification for bitumen primer for use in waterproofing & damp proofing.

IS:3414 	Code of practice for design and installation of joints in buildings.

IS:3550	Methods of test for routine control for water used in industry.

IS:3558	Code of practice for use of immersion vibrators for consolidating concrete.

IS:3696	Safety code for scaffolds (Part I ladders & II)

IS: 3812-2	Specification for pulverized fuel ash for use as admixture in cement mortar and concrete

IS:4014 	Code of practice for steel tubular scaffolding (Parts I & II)

IS:4031	Methods for physical tests for hydraulic cement.

IS:4130 	Safety Code for demolition of buildings.

IS:4326 	Code of practice for earthquake resistant design and construction of buildings.

IS:4461	Code of practice for joints in surface hydro-electric power stations.

IS:4656 	Specification for form vibrators for concrete.

IS:4925 	Specification for batching and mixing plant.

IS:4990 	Specification for plywood for concrete shuttering work.

IS:4995 	Criteria for design of reinforced concrete bins for the   storage  of granular and powdery materials. (Parts I & II)

IS:5121	Safety code for piling and other deep foundations.

IS:5256	 Code or practice for sealing joints in concrete lining on canals.

IS:5525	 Recommendations for detailing of reinforcement in reinforced concrete work.

IS:5624	Specification for foundation bolts.

IS:6461	Glossary of terms relating to cement concrete.

IS:6494 	Code of practice for water proofing of underground water reservoirs and swimming pools.

IS:6509 	Code of practice for installation of joints in concrete pavements.

IS:7193	Specification for glass fiber base coal-tar pitch and bitumen felts.

IS:7293	Safety code for working with construction machinery.

IS:7861	Code of practice for extreme weather concreting (Parts I&II)

IS:9012	Recommended practice for Shotcreting.

IS:9103 	Specification for admixtures for concrete.

IS:9417 	Recommendations for welding cold-worked steel bars for reinforced concrete construction.

IS:9595	 Recommendations for metal-arc welding of carbon and carbon manganese steels.

IS:10262	Recommended guidelines for concrete mix design.

IS:11384	Code of practice for composite construction in structural steel concrete.

IS:12118	Specification for two-parts poly sulphide.

IS:12200 	Code of practice for provision of water stops at transverse contraction joints in masonry and concrete dams.

IS:12269	43/53 Grade ordinary Portland cement.

IS:12600	Portland cement, low heat.

SP:23	Handbook of concrete mixes

SP:24	Explanatory Handbook on IS:456-1978

SP:34 	Handbook on concrete reinforcement and detailing.

- Sampling, testing and quality assurance

  - Facilities required for sampling materials, concrete, reinforcement, formwork, etc. in the field and in the laboratory shall be provided by the Contractor. The Contractor shall carry out all sampling and testing in accordance with the relevant Indian Standards and/or International Standards and this specification. Where no specific testing procedure is mentioned, the tests shall be carried out as per the prevalent accepted engineering practice to the directions of the Engineer. Tests shall be done in the field in the presence of the Engineer or his authorized representative and at a laboratory, approved by the Engineer, and the Contractor shall submit to the Engineer the test results in triplicate within three days after completion of any test.

  - The Contractor shall maintain records of all inspection and testing, which shall be made available to the Engineer. The Engineer at his discretion, may waive some of the stipulations for small and unimportant concreting operations and other works.

  - Work found unsuitable for acceptance shall be removed and replaced by the Contractor.  The work shall be redone as per specification requirements and to the satisfaction of the Engineer at no extra cost to the Owner.

  - Quality assurance programme

- The Contractor shall submit and finalize a detailed field Quality Assurance Programme within 30 days from the date of award of the contract, before commencement of work at site, according to the requirements of the specification. This shall include setting up of a testing laboratory, arrangement of testing apparatus/equipment, deployment of qualified/experienced manpower, preparation of format for record, field quality plan, etc.  On finalized field quality plan, the Owner shall identify, customer hold points, beyond which work shall not proceed without written approval from the Engineer.  The testing apparatus/equipment installed in the field laboratory shall be calibrated /corrected by the authorized persons as frequently as possible to give accurate testing results.

- Frequency of sampling and testing, etc. and Acceptance Criteria are given in respective sections.  However, the testing frequencies set forth are the desirable minimum and the Engineer shall have the full authority to carry out or call for tests as frequently as he may deem necessary to satisfy himself that the materials and works comply with the appropriate specifications.

Section 2 - Cast-in-situ concrete

- Scope

This section of the specification deals with plain or reinforced cement concrete for general use and in structures and covers the requirements for concrete, materials, their properties, storage, handling, grading, mix design, strength and quality, pouring at all levels, testing, casting, protecting, curing, finishing, etc.

- General requirement

  - The provision of IS:456 shall be followed as general guidance, along with all other relevant Indian Standards, unless otherwise specifically mentioned.

  - Before starting a concrete pour, the Contractor shall obtain the approval of the Engineer on a ‘Pour Card’ maintained for this purpose.  He shall obtain complete instructions about the materials and proportions, water cement ratio, etc. to be used, slump/workability, number of test cubes/samples to be taken, type of finishing to done, any admixture to be added, any limitation on size of pour and location for interruption of a pour in case of premature stopping of pour, etc.

  - The mixers and weigh-batchers, shall be maintained in clean and serviceable condition.  Accuracy of all equipment shall be periodically checked.  All concrete shall be mixed in mechanically operated batch mixers complying with IS:1791 and these shall be of approved make, with suitable provision for correctly controlling the water delivered to the drum.  Weigh batchers shall conform to IS:2722 and shall be capable of controlling the weights to within one percent of the desired value.

  - The Contractor’s procedures for casting massive concrete sections (as noted on the drawings or as identified by the Engineer) shall take account of the release of the heat of hydration, drying shrinkage behavior. The procedures shall be such that cracking or loss of strength of the concrete from these effects is prevented.  At least one week before commencing the construction of any massive concrete section, the Contractor shall submit, for approval of the Engineer, detailed proposals for placing the concrete together with supporting calculations to demonstrate the suitability of the methods.

- Materials

  - In general, all the materials used in the manufacture of concrete shall be in accordance with the Technical Specification for properties, storage and handling of common building materials, (vide module C2) which shall be deemed to form a part of this specification.

  - The Engineer shall have the right to inspect the sources of materials, method of procurement and storage of materials, method of procurement and storage of materials, quality control procedures, etc.

  - Cement

The cement used shall be the Ordinary Portland cement conforming to IS:269 or Portland Pozzolana cement conforming to IS:1489 or Portland slag cement conforming to IS:455 or any other type of cement, specified in IS:456 with the prior approval of the Engineer.  However, any special type of cement such as High strength cement or sulphate resisting cement, may be used under special circumstances.

  - Aggregates

- For reinforced concrete work, aggregates conforming to IS:383 & IS:2386 having a maximum size of 20 mm shall be used. For certain reinforced concrete works, aggregates having a maximum size other than 20 mm size shall also be used as called for in the drawings. However, for lean concrete provided as mud mat below structural concrete, maximum size up to 40 mm shall be used.

- Aggregates (coarse or fine) with a specific gravity below 2.6 shall not be used without special permission of the Engineer. Machine-made sand will be acceptable provided the constituent (rock/gravel) is sound, hard, dense and is acceptable to the Engineer.  Sand, natural gravel and crushed rock shall be prepared for use by such screening or washing, or both, as necessary to remove all objectionable foreign matter.

- Type of aggregates:  Petro graphic examination shall be carried out to ascertain the structure and rock type of aggregate including presence of strained quartz and other reactive minerals.  Moreover, in case the coarse aggregate sample is of composite nature, the proportions (by weight) of different rock types in the composite sample and petrographic evaluation of each rock should also be ascertained. While determining different rock type is in the composite sample, special emphasis should be given on identification of known reactive rocks like chalcedony, opal etc. and procedure laid down in IS:2430 for sampling of aggregates may be followed. The sample should not contain weathered rock and reduced to required quantity by quartering and coning.

- The results of petro graphic test, shall be submitted to the Engineer. The Engineer shall review the results on consultation with some specialist agencies, if required, to determine potential activity of the aggregate (siliceous minerals) which may lead to reaction of silica in aggregate with the alkalis of cement. In additional, potential of some aggregate like lime stone to residual expansion due to repeated temperature cycle is also to be reviewed. Further, the Contractor shall submit the results of Alkali aggregates reactivity carried out as per IS:2386 (Pt. VII).

- In case of any apprehension about the properties of the aggregate, the Engineer shall ask the Contractor to send samples of coarse and fine aggregate to any of the established research laboratory including National Council for, Cement and Building Materials (NCB), Ballabgarh for further testing. However, the Owner shall fix the agency and bear the cost of such testing. In case, it is established from the tests that the aggregates contain reactive silica which would react with alkalis of the cement, the Contractor shall be asked to change the source of supply of the aggregate and take additional measures as suggested.  In case aggregates indicate residual expansion, under repeated temperature cycle test, the material shall not be used for concreting of equipment foundations which are likely to be subjected under repeated temperature cycle. The Contractor shall use different type of aggregate as approved by the Engineer.

  - Admixtures

Admixtures in concrete for promoting workability, improving strength, entraining air for similar purposes may be used only after the written permission from the Engineer is obtained.  These shall be free from injurious amount of chloride, etc. Addition of admixtures should not reduce the specified strength or durability of concrete and should not have detrimental effect on reinforcement. The admixtures shall conform to IS:9103 and shall be of proven make and from a reputed manufacturer. Calcium chloride as accelerating admixture is not permitted to be used other than in mass concrete works. The Contractor shall produce latest test results carried out at approved Government Test Houses for the approval of the Engineer, before use details of admixtures have been covered under Section - 13.

- Water

  - Water used for mixing and curing shall be clean and free from injurious amounts of oils, acids, alkalis, sugar, organic materials or other substances that may be deleterious to concrete or steel. Potable water is generally considered satisfactory for mixing concrete.  The maximum permissible values of impurities shall be as given in clause no. 4.3 of IS:456-1978.

  - In case of doubt regarding development of strength, the suitability of water for making concrete shall be ascertained by the compressive strength and initial setting time tests specified in IS:456.

  - Average 28 days compressive strength of at least three 150 mm concrete cubes prepared with water proposed to be used shall not be less than 90% of the average strength of three similar concrete cubes prepared with distilled water. The cubes shall be prepared, cured and tested in accordance with IS:456.

  - The initial setting time of a concrete test block made with the appropriate cement and the water proposed to be used shall not be less than 30 minutes and shall  not differ by ± 30 minutes from the initial  setting time of control  test block prepared with the same cement and distilled water. The test shall be carried out as per IS:4031.

  - Where concrete, made from water, proposed to be used does not satisfy the above requirements and/or contains an excess of acid, alkali, sugar, salt or other deleterious, substances, then the Engineer may refuse to permit its use.  Sea water shall not be used for curing besides mixing in concrete.

- Grades of concrete

All concrete shall be "design mix concrete" as defined in IS:456, unless a nominal mix concrete such as 1:2:4, 1:3:6, 1:4:8 of 1:5:10 proportion is specified.  The proportion referred to is by weight (mass). The grades for 'design mix' concrete shall be designated M-15, M-20, etc. as specified in IS:456.  (20% replacement ratio of cement with fly ash shall be considered):

  - Nominal mix concrete

- Nominal mix concrete shall be used only for plain Cement concrete works and were shown on drawings or specifically allowed by the Engineer. Such concrete shall not require preparation of trial mixes and all such concrete shall be mixed in a mechanical mixer.  Proportions for nominal mix concrete shall be according to Table-3 of IS:456-1978. In addition, standard proportion by volume shall be used wherever specified.

- In proportioning concrete, the cement & fly ash shall be measured by (mass) weight.   The quantities of fine and coarse aggregates may be determined by volume (for corresponding weight) but preferably by weight.  If fine aggregates are moist, the amount of surface water shall be determined. Also, an allowance shall be made for bulking in case of volume batching, in accordance with IS:2386 (Part-Ill). Allowance shall also be made for surface water present in the aggregates, when computing the water requirement. All the above data shall be maintained properly, to the satisfaction of the Engineer.

- The recommended maximum water cement ratios are specified in Table 1.

Table 1: Recommended water - Cement ratio

| Nominal mix concrete | Quantity of water per 50 Kg. of cement (max.) |
| --- | --- |
| 1:5:10 | 60 litres |
| 1:4:8 | 45 litres |
| 1:3:6 | 34 litres |
| 1:2:4 | 32 litres |

- Nominal mix concrete 1:5:10 shall correspond to grade M5, 1:4:8 shall correspond to grade M7.5, 1:3:6 to grade M10 and 1:2:4 to grade M15 of IS:456.

- If Nominal mix concrete made in accordance with specified proportions does not yield the specified strength of the corresponding grade and fails to satisfy the requirements of “acceptance criteria for concrete” as specified in IS:456.  Such concrete shall be treated in the following manner:

  - In case the Engineer is satisfied that lower strength of concrete is attributed to material and workmanship of the Contractor, then such concrete shall be replaced by concrete of specified strength. The Engineer may however, also accept such lower strength concrete but such lower strength concrete shall be classified as belonging to the appropriate lower grade proportion.

  - In case the Engineer is satisfied that lower strength of concrete is not attributable to the Contractor, he may direct in writing to increase the cement content to obtain specified strength. Such extra cement shall also be considered for reconciliation purposes. The use of richer mix shall be continued until the Engineer instructs otherwise.

- Nominal mix proportion shall not be classified as higher-grade proportion either on the ground that the test strengths are higher than the minimum specified or in the case where the Engineer directs use of additional cement over the quantity specified for the particular mix proportion to achieve the minimum specified strength.

  - Design mix concrete

  - Mix design

  - Workability of concrete

- The workability of concrete shall be checked at frequent intervals. The workability of concrete measured in accordance with IS:1199 for every sample taken for testing shall be recorded with the corresponding cube test result.

- The degree of workability necessary to allow the concrete to be well compacted and to be worked into the corners of formwork and round the reinforcement to give the required surface finish shall depend on the type and nature of the structure and shall be based on experience and tests. The suggested ranges of values of workability for concrete for some placing conditions, measured in accordance with IS:1199 as stipulated under clause No. 6.0 of IS:456, are given below in Table-3, for guidance only.  In addition, in some special cases like casting of pile, very high degree of workability (up to 180 mm slump) shall be used.

Table 3: Limits of workability

| Placing | Degree of workability | Value of workability |
| --- | --- | --- |
| Concreting of shallow sections with vibration factor | Very Low | 20-10 seconds, Vee-bee time or 0.75-0.80 compacting. |
| Concreting of lightly reinforced section with vibration | Low | 10-5 seconds, Vee-bee time or 0.80-0.85 compacting factor. |
| Concreting of lightly reinforced section without vibration, or heavily reinforced sections with vibration | Medium | 5-2 seconds, Vee-bee time or 0.85-0.92 compacting factor or 25-75mm, slump for 20 mm aggregate (for smaller aggregate the values will be lower). |
| Concreting of heavily reinforced sections without vibration | High | Above 0.92 compacting factor or 75-125 mm slump for 20 mm aggregate (for smaller aggregate the values will be lower) |

Note: Notwithstanding the values given above, the slump to be maintained for work in progress shall be as per directions of the Engineer.

  - Mixing of concrete

- Concrete shall be mixed in a mechanical mixer conforming to IS: 1791.However, mixing shall preferably be done at a single central batching plant, conforming to IS:4925, situated within the area allocated for the Contractor’s particular use as shown on the drawing or as directed by the Engineer. The plant shall have a mechanically operated mixer of an approved size and type, capable of ensuring a uniform distribution of the materials throughout the mass and the mass is uniform in colour and consistency.

- Water shall not be added into the drum of the mixer, until all the cement and aggregates constituting the batch are already in the drum and dry mixed for at least one minute and are uniformly distributed. Water shall then be added and mixing of each batch shall be continued until there is a uniform distribution of the materials and the mass but in no case shall mixing be done for less than two minutes and for at least 40 revolutions after all the water and materials are in the drum. When absorbent aggregates are used or when the mix is very dry, the mixing time shall be extended as directed by the Engineer. Mixers shall not be loaded above their rated capacity as this prevents thorough mixing.

- The entire contents of the drum shall be discharged before the ingredients for the next batch are fed into the drum. No partly set or remixed or excessively wet concrete shall be used and it shall be immediately removed from site. Each time if the work stops for more than 30 minutes, the mixer shall be thoroughly cleaned and when the next mixing commences, the first batch shall have 10% additional cement.

- In exceptional circumstances and/or work in remote areas, hand mixing may be allowed by the Engineer, subject to adding 10% extra cement which shall be considered for reconciliation purposes. The mixing shall be carried out on watertight platform and mixing shall be continued till a uniform colour and consistency of the mix is achieved.

  - Concrete conveying

- Concrete shall be handled and conveyed as rapidly as practicable, from the place of mixing to the place of final laying, by approved means, before the initial setting of the cement starts. Concrete shall be conveyed in such a way that there is no segregation or loss of any of the ingredients and maintaining the required workability. If segregation does occur during transport, the concrete shall be remixed.

During very hot or cold weather, if directed by the Engineer, concrete shall be transported in deep containers which will reduce the rate of water loss by evaporation in hot weather and heat loss in cold weather, at no extra cost to the Owner.

- Conveying equipment for concrete shall be mortar tight, well maintained and thoroughly cleaned before commencement of concrete mixing. Such equipment shall be kept free from set concrete. Chutes shall not be used for transport of concrete without the written permission of the Engineer. The chute in case permitted to be used shall be of such size and design as to ensure practically continuous flow. Slope of the chute shall be so adjusted that the concrete flow without the use of an excessive quantity of water and without segregation of its ingredients. The delivery end of the chute shall be as close as possible to the point of deposit.

- Concrete may be conveyed and places by mechanically operated equipment, e.g., pumps or pneumatic placers only with the written permission of the Engineer, who shall also review the entire scheme for which comprehensive details shall be furnished by the Contractor.

  - Concrete placing

- Concrete shall be placed and compacted in its final position before the cement reaches the initial set and normally concrete shall be compacted in its final position within minutes of leaving the mixer.

- Where direct placement is not possible, the Contractor shall provide suitable arrangements such as chutes, tremie, elephant trunks, etc. to confine the movement of concrete as directed by the Engineer.  Concrete shall not be dropped from a height or handled in a manner which may cause segregation.

- If concrete is placed by pumping, the consistency shall be the minimum necessary for such conveyance of concrete.  Before commencement of regular pumping, the pipeline shall be lubricated by cement mortar (1:2), and once pumping commences, stoppages shall be avoided.

- Concrete shall not be placed in foundations on soft areas or where there is standing water or debris. Such soft areas shall be removed and filled with 1:4:8/1:3:6 nominal mix concrete, as directed by the Engineer.

For rock surfaces, it shall be ensured that the rock is not unsound. On sloping rock faces, rough steps or benches shall be formed and concrete shall not be placed on a sloping rock surface. Prior to pouring concrete, the rock surface shall be cleaned with a high-pressure water and air jet and kept wet for three hours. Also, before placing concrete, water shall be removed from depressions, the rock surface shall be dried and a 10mm thick cement sand mortar (1:6) layer shall be placed and worked into all crevices, cracks, depression, etc.

- The placing of concrete shall be a continuous operation with no interruption in excess of 30 minutes between the placing of continuous portions of concrete. Concrete shall be placed in continuous horizontal layers of 150 mm or higher thickness as directed by the Engineer and thoroughly compacted before placing next layer. The thickness of each layer shall be such that it will be deposited before the previous layer has stiffened. When placing concrete through reinforcing steel, care shall be taken to prevent segregation of the coarse aggregates.

- Approval by the Engineer of any of the materials and/or work as required herein shall not relieve the Contractor of his obligation to produce finished concrete in accordance with the drawings and specifications. Slots, openings, holes, pockets, etc. shall be provided in the concrete as directed by the Engineer.

- Slabs, beams and similar members shall normally be poured in one operation.  In special circumstances, with the approval of the Engineer, these can be poured in horizontal layers, but it must be ensured that the under layer is not already hardened.  Bleeding of under layer, if any, shall be effectively removed. Molding, throating, drip course, etc. shall be poured as shown on the drawings or as desired by the Engineer.

- After the concrete has been placed, it shall be spaded and thoroughly compacted by approved mechanical vibrators to a maximum subsidence without segregation and thoroughly worked around reinforcement or other embedded fixtures into the correct form and shape. Hand tamping in some cases may be allowed subject to the approval of the Engineer. Care must be taken to ensure that the inserts, fixtures, reinforcement and formwork are not displaced or disturbed during placing of concrete.

- Whenever vibration has to be applied externally, the design of formwork and the disposition of vibrators shall receive special consideration to ensure efficient compaction and to avoid surface blemishes. Surface vibrators and form attached vibrator shall not be permitted under normal conditions. Their use shall require written approval of the Engineer.

- Vibrators shall penetrate both the layer poured and the under layer to ensure good bond homogeneity and to prevent the formation of cold joints.  Immersion vibrators shall not be allowed to come in contact with steel reinforcement after start of initial set. Also, they shall not be allowed to come in contact with forms or finished surfaces.

- Immersion vibrators shall have a ‘no load’ frequency, amplitude and acceleration as per IS:2505 depending upon the size of the vibrator. Immersion vibrators shall be operated by experienced men. These vibrators shall be immersed not more than 450 mm apart and withdrawn when air bubbles cease to come to the surface. Such vibrators shall in no case be used to push concrete inside the forms and vibrators shall be withdrawn slowly.

- No concrete shall be placed in wet weather or on a water covered surface.  If there have been any signs of washing of cement or sand, the concrete shall be entirely removed immediately. Suitable precautions shall be taken in advance to guard against possible rains before leaving the fresh concrete unattended.

- Mass concrete shall be poured in lifts not exceeding 1.0 m in height unless otherwise indicated on drawings or as directed by the Engineer.  Horizontal lift shall not be more than 150 cm in thickness, according to provision of IS:457.

- Formwork and reinforcement shall be approved in writing by the Engineer before concrete is placed.  Concrete shall be placed only after all preparations for casting have been approved by the Engineer and approval given to proceed with the casting in writing on pour card to be maintained by the Contractor for this purpose and to be submitted along with the Contractor’s bills.

- Concrete, when deposited, shall have a temperature of not less than 5 degrees Centigrade and not more than 40 degree Centigrade.  When depositing concrete in very hot weather, precautions shall be taken so that the temperature of wet concrete does not exceed 40 degrees Centigrade while placing. This shall be achieved by stacking aggregates under the shade and keeping them moist, starting curing before concrete dries out, etc.  However, before mixing / placing concrete, when the above temperature conditions vary on either side, approval of the Engineer shall be obtained for the method of execution.

  - Protection and curing of concrete

- Newly place concrete shall be protected by approved means from rain, sun and wind.  Concrete placed below ground level, shall be protected from falling earth, during and after placing. Concrete placed in ground containing any deleterious substances, shall be kept free from contact with such ground or with water draining from such ground, during placing of concrete and for a period of at least three days or as otherwise instructed by the Engineer.

- The ground water around newly poured concrete shall be kept down to an approved level by pumping or other approved means of drainage. Adequate steps shall be taken to prevent floatation or flooding.  Steps, as approved by the Engineer, shall be taken to protect immature concrete from damage by debris, excessive loading, vibration, abrasion, mixing with earth or other deleterious materials, etc. that may impair the strength and durability of the concrete.

- As soon as the concrete had hardened sufficiently for the surface not to be marked, it shall be kept in a damp or wet condition by pounding or by covering with a layer of sacking, canvas, hessian or similar materials and kept continuously wet for atleast seven days after final setting. This period may be extended, at the discretion of the Engineer, up to fourteen days. Curing of horizontal surfaces exposed to drying winds shall begin immediately after the concrete has hardened. Concrete slabs and floors shall be cured for the periods mentioned above by flooding with water of minimum 25mm depth.

- Approved curing compounds may be used in lieu of moist curing with the permission of the Engineer. However, such permission may be granted only in specific cases. Such compounds shall be applied to all exposed surfaces of the concrete, as soon as possible after the concrete has set.

- Quantity of water applied shall be such as to prevent erosion of freshly placed concrete.

  - Construction joints

- When work has to be interrupted, the concrete shall be rebated and/or keyed at the joint to such shape and size as may be required by the Engineer or as shown on the drawings. All vertical construction joints shall be made with stop boards, which are rigidly fixed and slotted to allow for the passage of the reinforcing steel. In the case of water retaining structures, basements, tunnels, etc. water stop of approved material shall be provided, if so specified on the drawings or as directed by the Engineer.

- Construction joints shall be located as shown or described on the drawings. Where it is not described, the joints shall be in accordance with the following

  - In a column, the joints shall be formed about 75 mm below the lowest soffit of the beams framing into it, including haunches, if any. In flat slab construction, the joint shall be 75 mm below the soffit of the column capital.

  - Concrete in a beam shall be placed throughout without a joint. If unavoidable, the joint shall be vertical and within the middle-third of the span. When a beam intersects a girder, the joints in the girder shall be given an offset equal to a distance twice the width of the beam and additional reinforcement provided for shear.  The joints shall be vertical throughout the full thickness of the concrete member with suitable shear key wherever shown on the drawing.

  - A joint in a suspended floor slab shall be vertical at one quarter points of the span and at right angle of the principal reinforcement.

  - Construction joints in equipment foundations shall not be provided without specific concurrence of the Engineer.

  - Vertical construction joints in water retaining structures shall not be permitted unless shown on the drawings.

However, if the Contractor desires any adjustments in the location of construction joints (to suit site conditions) from those shown on drawings or from those explained above, he shall obtain prior approval from the Engineer.

- Before fresh concrete is placed, the cement skin of the partially hardened concrete which was poured earlier shall be thoroughly removed and the surface made rough and aggregate exposed, by wire brushing, hacking, water jetting, air jetting or any other method as directed by the Engineer. The rough surface shall be thoroughly wetted for about 1/2 hour and shall be dried and coated with 10 to 15 mm thick layer of 1:1 freshly mixed cement and sand slurry. Special care shall be taken to see that the first layer of concrete placed after a construction joint is thoroughly rammed against the existing layer.

- In forming a joint, concrete shall not be allowed to slope away to a thin edge. The locations of construction joints shall be planned by the contractor well in advance of pouring and they will have to be approved by the Engineer. The Contractor's proposals shall include at least the location of construction joints, the sequence of pouring, formwork details and their stripping times.

- Where the concrete has not fully hardened, all laitance shall be removed by scrubbing the wet surface with wire or bristle brushes. Care being taken to avoid dislodgement of particles of aggregates. The surface shall be thoroughly wetted and all free water removed. The surface shall then be coated with neat cement slurry. On this surface, a layer of concrete not exceeding 50 mm in thickness shall first be placed shall be well rammed against old work, particular attention being to corners and close spots. Work thereafter, shall proceed in the normal way.

- For multiple lift work a suitable gap shall be maintained between setting of the earlier placed concrete and the commencement of concrete pour. After depositing concrete in columns, piers or walked time gap of minimum 4 hours, preferably 24 hours shall be maintained before depositing concrete in beams, girders or slabs, supported there in order to avoid cracking due to settlement.

  - Work in extreme weather conditions

During hot weather (atmospheric temperature above 40 degree centigrade) of cold weather (atmospheric temp at 5 degrees centigrade and below) the concreting shall be done as per the procedures and precautions set out in IS:7868 (Parts I and II).

  - Cleaning and finishing of concrete

  - All concrete surfaces shall have an even and clean finish free from honeycombs, air bubbles, fins or other blemishes unmarred, reasonable smooth. The formwork joint marks on concrete work exposed to view shall be rubbed with carborandum stone and defects patched up with paste of cement sand mortar (1: 2) and cured. The finish shall be made to the satisfaction of the Engineer. Concrete surfaces to be subsequently plastered or where brick work is to be built against them, shall be adequately hacked as soon as the form is stripped off so that proper bond can develop.

  - Immediately after removal of forms, the concrete shall be inspected and defective areas as pointed out by the Engineer shall be removed partially or entirely as directed. Holes, left by form bolts, etc. shall be filled-up and made good with cement sand mortar of approved mix. All superficial defects such as honeycombing, rough patches, etc. shall be similarly made good. If the defective area is at a vulnerable location, e.g. at the ends of beams & columns etc. then it may be necessary to cut out the member completely or in part and reconstruct as directed by the Engineer. If epoxies have to be used, the same shall be subject to the approval of the Engineer. Poured concrete affected by faulty formwork shall be removed totally and replaced. If so directed, the Contractor shall have to resort to grouting / shotcreting.

  - A smooth finish shall be obtained with the use of forms having smooth and even surfaces and edges. Panels and form linings shall be of uniform size and be as large as practicable and installed with closed joints. Upon removal of forms, the joint marks shall be smoothened off and all blemishes, projections etc. removed leaving the surfaces reasonably smooth and unmarred.

  - Where integral cement concrete finish is called for, the surface shall be compacted and then floated and treated with a straight edge and any high and low spots eliminated. The work shall be carried out as per IS:2571.

- Sampling, testing and quality assurance including construction tolerances

  - General

- Concrete cubes for works tests shall be cured under laboratory conditions, except when in the opinion of the Engineer, extreme weather conditions prevail at which time, these may require curing under job conditions.

- For the purposes of statistical analysis, any substandard cube result, which in the opinion of the Engineer, is due to improper sampling, molding or testing shall be discarded and a dummy result shall be substituted. The value of a dummy result shall be equivalent to the average value of the cubes from the same grade of concrete tested immediately before and after the discarded result. The number of such substandard cubes shall not exceed 5%.

- If the 'strength' of the laboratory-controlled cubes, for any portion of the concrete work, falls below the compressive strength specified, the Engineer shall have the right to order a change in the proportions or the water content for the remaining portion of the surface.

- If the 'strength' of the works cured test cubes falls below the specified strength, the Engineer shall have the right to require provisions for temperature and moisture control during the period of curing as necessary to secure the required strength, and may require retest in accordance with the standard method of securing, preparing and testing specimens from hardened concrete for compressive and flexural strengths, or load tests to be made on the portion of the building so affected. All such tests shall be made at the Contractor's expense.

- Unacceptable concrete work shall be dismantled by the Contractor and replaced by fresh work, meeting the specification requirements. In the course of dismantling, if any damage is done to the embedded items or adjacent structures, the same shall be made good, by the Contractor, to the satisfaction of the Engineer, at no extra cost to the Owner.

- Only as a very special case and that too in non-critical areas, the Engineer may accept concrete work which is marginally unacceptable as per the criteria laid down in IS:456. For such accepted work, payment shall be made at a reduced rate prorate to the concrete cube strength obtained, against that stipulated.

- Before placing concrete, the inside of forms shall be checked to ensure that they are clean and thoroughly wetted or adequately treated. So as to prevent absorption of water from the concrete.

- Ultrasonic tests on the foundations of major equipment to ascertain the quality and grade of concreting shall be carried out. The Owner shall arrange for the specialized agency for conducting the test at his cost. The Contractor shall provide all the necessary facilities and arrangement for conducting the test at site in terms of access, scaffolding etc. In case of any defects, the Contractor shall rectify the same as directed by the Engineer.

- Rebound hammer test shall be carried out for ascertaining the quality of concrete work, as directed by the Engineer.

- Test shall be conducted for the water tightness of the liquid retaining structures as per IS:3370 and IS:6494. The details and sequence of tests shall be as given hereunder:

  - All arrangements, including supply of water for testing purposes, shall be kept ready when the tank is nearing completion.

  - Water supply to the tank shall be in stages of 300 to 450 mm height in order to check the water tightness of the tank and location of leakage of various levels.

  - The permissible drop in level in 24 hours shall be 6 mm in case of covered reservoir/tank and 12 mm in the case of open reservoir/tank.

  - The leakage points shall be marked and separately treated after dewatering.

  - The reservoir/tank shall be retested for water tightness after rectification.

For basement type structures like cable vault, track-hopper, tunnel, neutralizing pit, etc. the Contractor shall examine the water tightness against ingress of sub-soil water.

Frequency of sampling and testing including the methods of conducting the tests shall be as given in Annexure B.

  - Sampling of concrete

  - Unless otherwise specified, the tolerance in construction shall be as follows:

  - Acceptance criteria

The acceptance criteria of concrete shall be in accordance with clause no. 15 of IS:456- 1978. However, in exceptional circumstances, the Engineer may, at his discretion, accept a concrete of lower strength than that specified at reduced rates. The concrete shall be deemed to comply with the strength requirements if:

- Every sample has a test strength not less than the characteristic value or

- The strength of one or more samples, though less than the characteristic value, in each case is not less than the greater of :

  - The characteristic strength minus 1.35 times the Standard Deviation and

  - 0.80 times the characteristic strength; average strength of all the samples, is not less than the characteristic strength + [1.65 - 1.65/ square root of (No. of samples)] times the standard deviation.

  - Load test

If any work is found unacceptable whereupon the Engineer requires its removal and reconstruction, the Contractor may request that it should be load tested in accordance with the provision of clause no. 16.50 of IS:456- 1978 as given below:

- The test load shall be 25 percent of the maximum superimposed load for which the structure or element was designed. This load shall not be applied earlier than 28 days after the effective hardening of concrete. This test load shall be maintained for 24 hours and during the entire duration of the test, struts, strong enough to take the whole superimposed, dead and other loads shall be placed in position, leaving a small gap under the members.

- The maximum deflection shall be measured after the test load is in position for 24 hours. Thereafter, the test load shall be removed.

- If 24 hours after the removal of the load, the structure does not show a recovery of at least 75 percent of the maximum deflection, registered as in (b) above, the test shall be repeated after a lapse of 72 hours. The structure shall be considered to have failed to pass the test if the recovery after the second test is not at least 80 percent of the maximum deflection during the second test.

- If the maximum deflection in mm, shown during 24 hours under load, is less than 40 l sq / D, where I is the effective span in metres and D is overall depth of the section in mm, it is not necessary for the recovery to be measured and the recovery position of the above mentioned clause 10.5 (c) will not apply.

# Section 3 - Reinforcement

- Scope

  - This section of the specification deals with reinforcement for all reinforced concrete works and covers the requirement of materials, their properties, storage, handling, furnishing of bar bending schedules and the cleaning, bending, binding and placing of reinforcement with suitable cover blocks. This shall also include the supply of reinforcement, wherever required.

- General requirements

  - The Contractor shall prepare and furnish to the Engineer, bar bending schedules for all RCC works for his review and approval. No work shall commence without the approval of bar bending schedule by the Engineer, in writing.

  - The Contractor shall have to obtain prior written approval from the Engineer, if he desires any adjustments in diameter or spacing of reinforcement. However, the Contractor shall modify the bar bending schedule, when a particular type and size of reinforcement would not be available, with the approval of the Engineer.

- Materials

  - All steel for reinforced concrete works shall be in accordance with Technical Specification for Properties, Storage and Handling of common Building Materials, (vide module C2) which shall be deemed to form the part of this Specification.

  - All bars shall be thoroughly cleaned before being fabricated. Pitted and defective bars shall not be used.

- Bending and placing

  - Bending

- Reinforcing bars supplied bent or in coils, shall be straightened before these are cut to size. Straightening of bars shall be done in cold and without damaging the bars. This is to be considered as a part of reinforcement bending and fabrication work.

- Unless otherwise specified, reinforcing steel shall be bent in accordance with procedure specified in IS:2502 and/or as approved by the Engineer. Bends and shapes shall comply strictly with the dimensions shown on the approved bar bending schedules and they shall be rechecked by the Contractor before bending and he shall be entirely responsible for their correctness. Bars correctly bent, shall only be used. Unless specified otherwise or directed by the Engineer, the detailing of reinforcement shall be in accordance with IS:5525 and SP:34.

- No reinforcement shall be bent, when in position in the work without approval of the Engineer, whether or not it is partially embedded in concrete. Where the reinforcement bars are bent aside, at construction taken to ensure that, at no time, the radius of the bend is less than 4 times the bar diameters for plain mild steel or 6 times the bar diameters for deformed bars. Care shall also be taken while bending back bars, to ensure that the concrete around the bar is not damaged.

- Welding of bars to obtain continually shall not be allowed, particularly for cold twisted bars, unless specifically approved by the Engineer. If welding is approved, the work shall be carried out as per IS:2751 and IS:9417, according to the best practice and as directed by the Engineer.

  - Placing in position

- All reinforcement shall be accurately fixed and maintained in position as shown on the drawings by such approved means as steel chairs, and/or concrete spacer blocks as per IS:2502. Bars intended to be in contact at crossing points by two numbers annealed steel wire of 0.9 mm to 1.6 mm size conforming to IS:280 in such a manner that they do not slip over each at the time of fixing & concreting. The tying of bars shall be in crisscross manner.

- Binders shall tightly embrace the bars with which these are intended to be in contact and shall be securely held. The vertical distance between successive layers of bars shall be maintained by provision of spacer bars. These shall be so spaced that the main bars do not sag perceptively between adjacent spacers.

Bundled bars shall be provided wherever shown on the drawing to facilitate concreting. Location of laps and development lengths, shall be as indicated on the drawings.

- The placing of reinforcement shall be completed well in advance of concrete pouring. Just prior to concrete pouring, the reinforcement shall be checked by the Engineer, for accuracy of placement and cleanliness. Necessary corrections, as directed by the Engineer shall be carried out. Care shall be taken to ensure that projecting ends of ties and other embedded metal do not encroach into the concrete cover. Where concrete blocks are used for ensuring the cover and positioning of reinforcement, these shall be made of mortar 1:2 (1 cement : 2 sand) by volume and cured for at least seven days. The sizes and locations of the concrete blocks shall be approved by the Engineer. The 28 days crushing strength of cover blocks shall be at least equal to the specified strength of concrete in which the blocks will be embedded.

- Laps and anchorage length of reinforcing bars shall be in accordance with IS:456, unless otherwise specified. If the bars in a lap are not of the same diameter, the smaller diameter will guide the lap length. Laps shall be staggered as far as practicable and as directed by the Engineer and not more than 50% of bars shall be lapped at a particular section. Mechanical connections, for splicing reinforcement bars in congested locations may be used by the Contractor, only if approved by the Engineer. Reinforcement bars shall not be lapped unless the length required exceeds the maximum available lengths of bars at site.

- Cover to reinforcement

- Unless shown otherwise on the drawings, minimum clear concrete cover for reinforcement (exclusive of plaster or other finishes) shall be as follows: -

  - At each end of a reinforcing bar, not less than 25 mm, nor less than twice the bar diameter.

  - For a longitudinal reinforcing bar in a column, 40 mm or bar diameter whichever is more. 25 mm cover may be adopted for columns of minimum dimension 200 mm or under and with longitudinal reinforcement diameter not exceeding 12 mm.

    - For longitudinal reinforcing bars in a beam, not less than 25 mm or less than the bar diameter.

    - For reinforcement in slabs and walls; not exposed to weather or ground not less than 15 mm nor less than the bar diameter.

    - For bottom reinforcement in footings: 75 mm, if concrete is laid against the ground or 40 mm if laid on a layer of lean concrete.

    - For retaining walls, grade beams, top and sides of footings and similar surfaces exposed to weather or ground; 50 mm for bars larger than 16 mm and 40 mm for bars up to 16 mm.

    - For concrete members exposed to the action of harmful chemicals, acids, alkalis, atmosphere, sulphurous smoke, sea water etc., the cover shall be as shown on the drawings.

    - For liquid retaining structures; 40 mm or diameter of main bars, whichever is larger. This shall be increased to 50 mm in case of sea water or corrosive environment.

- Clean distance between reinforcing bars shall be in accordance with IS:456 or as shown on drawings.

- Sampling, testing and quality assurance

  - General

Sample bent bars shall be checked to ensure that they conform to the bar bending schedules. Reinforcement in position shall be checked for proper positioning, and rigidity, cover, spacing of bars, placement of chairs and spacers, etc. Also it shall be checked that all bars at crossings are properly tied.

  - Tolerance

Tolerance in construction, unless otherwise specified or as approved by the Engineer shall be as follows:

## Description of item/Structural	Permissible Deviation element		in mm (Max.)

| Placing of reinforcement For effective depth 200 mm or less | +10 | -5 |  |
| --- | --- | --- | --- |
| For effective depth more than 200 mm | +15 | -10 |  |
| Cover to reinforcement |  | -5 |  |
| Cutting of reinforcement When minimum length specified | +75 | - |  |
| When maximum length specified When maximum or minimum length not specified | - +75 | -50 -25 |  |

NOTE:- For any other references regarding permissible deviations shall be referred to the tolerance limit enclosed Annexure F.

  - Frequency of sampling and testing of reinforcement work shall be as given in Annexure B.

Annexure - "B" Table - 4

Frequency of sampling and testing

| Sl. No. | Nature of test/ characteristics | Method of test | No. of samples & frequency of test | Remarks |
| --- | --- | --- | --- | --- |
| . | Coarse aggregates |  |  |  |
| a) | Particle size and shape | IS:2386(Pt.1) | One per 100 cum. or part thereof or change of source whichever is earliest | Result to be as per the requirement of design mix, subject to variations within the limits specified in relevant Indian Standards. |
| b) | Moisture content | IS:2386(Pt.3) | Once for each stack of 100 cum. or part thereof except during monsoon when this has to be done every day before starting of the work. | Accordingly water content of the concrete shall be adjusted. |
| c) | Specific gravity, density, voids, absorption. | IS:2386(Pt.3) | Once in 12 weeks or change of source whichever is earlier | These tests shall be carried out while establishing design mix and results to be intimated. |
| d) | Mechanical properties, crushing value, abrasion value and impact value. | IS:2386(Pt.4) | Once per source | Acceptance norms shall be as per IS:383 |
| e) | Soundness | IS:2386 (Pt.5) | Once per source | Acceptance norms shall be as per IS:383. |
| f) | Reaction with alkali. | IS:2386 (Pt.7) | Once per source | These tests shall be carried out while establishing design |

| Sl. No. | Nature of test/ characteristics | Method of test | No. of samples & frequency of test | Remarks |
| --- | --- | --- | --- | --- |
|  |  |  |  | mix and result to be intimated. Acceptance shall be as per IS:2386 (Pt.7) and Clause 7.4C of this specification. |
| g) | Flakiness and petro- graphic examinations | IS:2386 | This is to be done once and should be repeated in case the source is changed. | These tests shall be carried out while establishing design mix and results to be intimated. |
| h) | Deleterious materials | IS:2386 (Pt.2) | Once per source | Results should be within the limit as specified in relevant Indian Standards and in this Specification. |
| 2. | Fine aggregates/ sand |  |  |  |
| a) | Particle size and shape. | IS:2386(Pt.1) | One per 100 cum. or part thereof or change of source, whichever is earlier. | Should be as per the requirement of design mix, subject to variation within the limit as specified in relevant IS Codes. |
| b) | Specific gravity, density, voids, adsorption and bulking. | IS:2386 (Pt.3) | Once in 12 weeks or change of source whichever is earlier | These tests will be carried out while establishing design mix and results to be intimated. |
| c) | Bulk age, moisture content (Routine test) | IS:2386 (Pt.3) | To be done every day before start of work. | Volume of sand and weight of water shall be adjusted as per bulk age and moisture content. |

| Sl. No. | Nature of test/ characteristics | Method of test | No. of samples & frequency of test | Remarks |
| --- | --- | --- | --- | --- |
| d) | Silt, clay deleterious materials, organic impurities. | IS:2386 (Pt.2) | Once per source and to be repeated, if source is changed. | Volume of sand and weight of water shall be adjusted as per bulk age and moisture content. |
| e) | Soundness and Petrographic examination. | IS:2386 (Pt. 5 & 8) | Once per source. | Acceptance norms shall be as per IS:383. |
| f) | Mortar making properties. | IS:2386 (Pt.6) | -do- | Acceptance norms shall be as per IS:383. |
| g) | Reaction with alkali. | IS:2386(Pt.7) | Once per source | Acceptance norms shall be as per IS:383 and IS:2386 (Pt.7). |
| 3. | Cement |  |  |  |
| a) | Setting time | IS:4031 | One sample of each received from stores. | Acceptance norms shall be as per relevant Indian Standard |
| b) | Compressive Strength | IS:4031 | -do- | -do- |
| 4. | Water |  |  |  |
|  | Harmful substances, pH value, initial setting time, compressive strength. | IS:3025, IS:4031 & IS:516 | Once a month for each source | Acceptance norms shall be as per Cl.4.3 of IS:456- 1978. |
| 5. | Concrete |  |  |  |
| a) | Workability (Slump and compaction factor) | IS:1199 | One sample every two hours from every mixing plant. | Acceptance value shall be as per Cl. 6. of IS:456- 1978. |

| Sl. No. | Nature of test/ characteristics | Method of test | No. of samples & frequency of test | Remarks |
| --- | --- | --- | --- | --- |
| b) | Crushing Strength | IS:516 | As per Cl. 14.2.2 ofIS:456-1978 for initial period One sample of six cubes per 150 cum or part thereof for mass concrete for subsequent period. | Acceptance criteria shall be as per Cl. 5 of IS:456- 1978. A minimum of 3 (Part- 7) specimens shall be tested for 28 days strength. |
| c) | Water-cement ratio | IS:1199 | At random at the time of batching | According to mix design |
| d) | Cement Content | IS:1199 | -do- | -do- |
| e) | Finished dimensions | Physical measurement | All structures | Acceptance as per Specification |
| 6. | Form work a) Staging (Curability strength & soundness of staging, joints, adequacy of its foundation and specific level) | Visual | Each member | Any staging intended for use shall be approved by the Engineer for its durability and strength |
|  |  |  |  | After erection of staging, nominated representatives of Engineer shall check the soundness of the staging as a whole, its joints, adequacy of its foundation and the specific levels. |
|  | b) Shuttering |  |  |  |

| Sl. No. | Nature of test/ characteristics | Method of test | No. of samples & frequency of test | Remarks |
| --- | --- | --- | --- | --- |
|  | i) Materials | Visual | Random | Formwork materials shall be strictly as per specifications and approved of the Engineer. Materials for formwork shall be unwrapped, thoroughly clean and without broken or damaged edges either due to repetitive use or otherwise. Oiling of form work before concreting shall be resorted to. |
|  | ii) Joints | Visual | Random | Joints shall be leak proof to avoid loss of liquid |
|  | iii) Dimensions and plumb | Physical measurement | Each member and before every lift. | Tolerance as per Specification |
| 7 | Reinforcement |  |  |  |
|  | a) Placement | Visual | each | The bar bending schedule with the necessary hooks, laps, covers, spacers and chairs shall be 100% checked for all concreting works before start of the work. |
|  | b) Cutting tolerance | Physical measurement | Random | Tolerance shall be as per specification. |

Sub-Section - C4 Technical specification for masonry and allied works

# Sub-Section - C4

Technical specification for masonry and allied works

Contents

## Clause no.	Description					Page nos.

- Scope

- General requirements

- Codes and standards

- Brick masonry

- Fly ash brick masonry

- Stone masonry

- Mouldings and cornices

- Plinth protection

- Damp Proof Course (DPC)

- Dismantling and demolition

- Sampling testing and quality control

Section - C4: Technical specifications for masonry and allied works

- Scope

This section of the specification covers furnishing, installation including handling, transportation, batching, mixing, laying, scaffolding, centering, shuttering, finishing, curing, protection and repairing till handing over of brick masonry and allied works including DPC, plinth protection and dismantling.

- General requirements

  - The Contractor shall furnish all skilled and unskilled labour, plant, equipment, scaffolding, materials, etc. required for complete execution of the work in accordance with the drawings and as described herein and/or as directed by the Engineer.

  - All workmanship shall be in accordance with the latest standards and best possible practice. Masonry work shall be true to line & level as shown on drawings. All such masonry shall be tightly built against structural members and bonded with dowels, anchors, inserts, etc., as shown on the drawings.

  - The Contractor shall carry out all works for settling out the building lines, locating the co-ordinates and establishing the reduced levels (RL's) on the basis of reference grid lines and benchmark, which shall be furnished by the Owner, at one or more locations.

  - Any approval, instructions, permission, checking, review, etc. whatsoever by the Engineer shall not relieve the Contractor of his responsibility and obligation regarding adequacy, correctness, completeness, safety, strength, quality, workmanship, etc.

- Codes and standards

  - All applicable standards, acts and codes of practice referred to shall be the latest editions including all applicable official amendments and revisions. A complete set of all these documents shall generally be available at site, with the Contractor.

  - In case of conflict between this specification and those (IS Standards, Codes etc.) referred to in clause 3.3, the former shall prevail.

  - Some of the applicable Indian Standards, Codes, etc. are referred to here below:

IS:1127	Recommendations for dimensions and Workmanship of

Natural Building Stones for Masonry Work.

IS:1597	Code of practice for construction of Stone Masonry.

IS:1905	Code of Practice for Structural Safety of Buildings - Masonry walls.

IS:2116	 Specification for sand for masonry mortars.

IS:2185	Specification for Hollow cement concrete blocks IS:2212	Code of Practice for Brickwork.

IS:2250	Code of Practice for preparation and use of masonry mortar.

IS:2572	Code of Practice for construction of Hollow concrete block masonry

IS:3414	Design and installation of joints in buildings. IS:3696	 Safety code for scaffolds and ladders.

IS:4130	Safety code during demolition of buildings.

IS:4326	Code of practice for earthquake resistant design and construction of buildings

IS:12894	Fly ash lime bricks specifications.

SP:20	Explanatory handbook on masonry code.

- Brick masonry

  - Materials

Properties of common building materials for the construction of brick masonry, viz. burnt clay bricks, sand lime and cement shall be in accordance with the technical specification for 'Properties, Storage and Handling of Common Building Materials' (vide Mode C2). Besides clay bricks, other type of bricks like, fly ash-lime bricks cured by autoclave process shall also be used, whenever specified, or shown on the drawing.

- Fly ash brick masonry

  - Materials

Properties of common building materials for the construction of brick masonry, viz. fly ash bricks, sand lime and cement shall be in accordance with the technical specification for 'Properties, Storage and Handling of Common Building Materials' (vide Mode C2). Besides fly ash bricks, other type of bricks like, fly ash-lime bricks cured by autoclave process shall also be used, whenever specified, or shown on the drawing.

  - Mortar

IS: 2250 shall be followed as general guidance for preparation and use of mortar. Only cement &Fly ash-sand mortar shall be used. Lime shall be added for composite mortar with specific approval of the Engineer.

Unless otherwise specified, mortar for brickwork having one or more brick thickness shall be 1 part cement & fly ash (20% replacement ratio of cement with fly ash): and 6 parts sand by volume. Mortar for half-brick thick walls shall be 1 part cement & fly ash (20% replacement ratio of cement with fly ash): and 4 parts sand by volume. Richer mix proportion shall be used, whenever specified or as per design requirement. Mortar shall meet the compressive strength requirement as per IS: 2250 and IS: 1905.

Sand shall conform to IS: 2116. Grading of sand when tested as per IS: 2386 shall be as specified in Table -1.

Table 1: Grading of sand for use in masonry mortars

| 15 sieve designation 15:460 (Part - 1) | Percentage passing by mass | Method of test |
| --- | --- | --- |
| 4.75mm | 100 | IS:2386 |
| 2.36mm | 90 to 100 | (Part-I) |
| 1.18mm | 70 to 100 |  |
| 600 micron | 40 to 100 |  |
| 300 micron | 5 to 70 |  |
| 150 micron | 0 to 15 |  |

Sand, whose grading falls outside the specified limits due to excess or deficiency of coarse or fine particles, may be processed to comply with the standard by screening through a suitably sized sieve and/or blending with required quantities of suitable sizes of sand particles. Based on test results and in the light of practical experience with the use of local materials, deviation in grading of sand given in Table-1 may be considered by the Engineer. The various sizes of particles of which the sand is composed, shall be uniformly distributed throughout the mass. The required grading may often be obtained by screening and/or by blending together either natural sands or crushed stone screenings, which are by themselves of unsuitable grading.

Cement, fly ash (20% replacement ratio of cement with fly ash): and sand shall be thoroughly mixed dry in a mechanical mixer and water shall then be added to obtain a mortar of the consistency of a stiff paste, care being taken to add just sufficient water for the purpose. Water shall be clean and free from injurious amount of deleterious matter such as oil, acid alkali, salt and vegetable growth. Hand mixing may be allowed by the Engineer on clean approved platform in special cases only. Mortar shall be used as soon as possible after mixing, before it begins to set and preferably within 30 minutes after water is added to the dry mixture. Mortar unused for more than 30 minutes shall generally be rejected and removed from site of work. However, the Engineer may allow the use of mortar up to 2 hours.

Surplus mortar droppings while laying masonry, if received on a surface from dirt, may be mixed with fresh mortar if permitted by the Engineer, where direct for addition of extra cement and this shall be implemented.

  - Laying

IS:2212 shall be followed as general guidance for construction of brick masonry Vat/tank of suitable size shall be provided by the Contractor for soaking of bricks. Bricks shall be soaked in water before use for a period generally not less than 6 hours so that the water just penetrates the whole depth of the bricks. Bricks shall be laid in by hand and not thrown inside the tank. Bricks shall be taken out sufficiently in advance so that these are skin dray at the time of laying.

Bricks shall be laid in English Bond unless otherwise specified. Half or cut bricks shall not be used except where necessary to complete the bond. Closers in such cases shall be cut to the required size and used near the ends of the walls, next to quoin headers.

Bricks shall be laid generally with frogs upwards. A layer of mortar shall be spread on the full width and over a suitable length of the lower course. Each brick shall be properly bedded and set home (in position) by gently tapping with the trowel handle or with a wooden mallet. It's inside face shall be buttered with mortar before the next brick is laid and pressed against it. On completion of a course, all vertical joints shall be fully filled from the top with mortar. The thickness of joints shall be kept uniform and shall not exceed 10 mm. Bricks shall be so laid that all joints are full of mortar.

All face joints shall be raked to a minimum depth of 15 mm by raking tools during the progress of brickwork, when the mortar is still green, so as to provide proper key for the plaster or pointing to be done. When plastering or pointing is not required to be done, the joints shall be struck flush and finished at the time of laying.

Brickwork in walls shall be taken up truly plumb. All courses shall normally be laid truly horizontal unless indicated to be laid on slope and all vertical joints shall be truly vertical. Vertical joints in alternate courses shall come directly one over the other. Brick wall shall be construed with at least one plain face with proper alignment.

All connected brickwork shall be carried up simultaneously and no portion of work shall be left more than one metre below the rest of the work. Where this is not possible, in the opinion of the Engineer, the work shall be raked back according to bond (and not toothed) at an angle not steeper than 45 deg. The work done per day should not be more than one metre height.

All iron fixtures, pipes, water outlets, holdfasts for doors and windows, etc. which are required to be built into the brickwork shall be embedded in their correct position in mortar or cement concrete as the work proceeds as per directions of the Engineer.

All brickwork shall be built tightly against columns, floor slabs or other structural parts and around door and window frames with proper distance to permit caulked joint. Where drawings indicate that structural steel columns and spandrel beams are to be partly or wholly covered with brickwork, the bricks shall be laid closely against all flanges and webs with all spaces between the steel and brickwork filled solid with mortar not less than 10mm in thickness.

The top courses of all plinth, parapet, steps and top wall below CRC shall be laid with brick on edge (other than modular size bricks) unless otherwise specified. Care shall be taken that the bricks forming the top courses and ends of walls are properly radiated and keyed into position as shown on the drawings.

Scaffolding shall be strong enough to withstand all the dead, live and impact loads which are likely to come upon it. It shall also be so designed as to ensure the safety of the workmen using them.

For all brick masonry except for exposed brickwork, single scaffolding shall be permitted. In such cases, the inner end of the horizontal scaffolding pole shall rest in a hole provided only in header course for the purpose. Only one header for each pose shall be left out. Such holes for scaffolding shall, however, not be allowed in pillars/columns less than one metre in width. The holes left in masonry works for scaffolding purposes shall be filled and made good before plastering.

In case of joining old brickwork with new brick work, the old work shall be toothed to the full width of the new wall and to the dept of quarter of a brick in alternate courses. It shall be cleaned of all dust, loose mortar, etc., and thoroughly wetted before starting new brick work. Thickness of each course of new work shall be made equal to the thickness of the corresponding course of the old work by adjusting thickness of horizontal mortar joints.

The face of the brickwork shall be cleaned on the same day on which brickwork is laid and all mortar dropping removed promptly.

Template (bed-block) of plain or reinforced cement concrete shall generally be provided to support ends of RCC beams. Top surface of the wall shall be suitably treated as per direction of the Engineer so as to minimise the friction to movement of the concrete slab over the bearing.

Brickwork shall be protected from rain by suitable covering when the mortar is green. Masonry work shall be cured by keeping it constantly moist on all faces for a minimum period of seven days. Brickwork carried out during the day shall be suitably marked indicating the date on which the work is done so as to keep a watch on the curing period.

  - Half brick masonry

The work shall be done in the same manner, as mentioned in 4.03 except that all course shall be laid with stretchers. In cases where reinforcement is considered necessary from structural consideration, 2 nos. 8 mm dia bars shall be provided generally at every 4th layer of bricks or as specified on the drawings. Before laying reinforcement, it shall be cleaned of rust and loose flakes with a wire brush. They shall be securely anchored at their ends where the partitions bond. Half the mortar thickness for the bedding joint shall be laid first and then 8mm dia bars laid straight out near each face of the brickwork maintaining a side cover of 12mm mortar. Subsequently the other half of the mortar thickness shall be laid covering the reinforcement fully.

  - Exposed brickwork

Exposed brickwork i.e. brickwork is superstructure which is not covered by plaster shall be as shown on the drawings and shall be done by specially skilled masons. All courses shall be laid truly horizontal and all vertical joints shall be truly vertical. Vertical joints in alternate courses shall come directly one over the other. Thickness of brick courses shall be kept uniform and for this purpose wooden straight edge with graduations indicating thickness of each course including joint shall be used. The height of window sills, bottom of lintels and other such important points in the height of the wall shall be marked on the graduated straight edge. Masons must check workmanship frequently with plumb, spirit level, rule and string.

For all exposed brick work, double scaffolding having two sets of vertical supports shall be provided. The supports shall be sound and strong, tied together with horizontal pieces over which scaffolding planks shall be fixed.

If face bricks are specified on the drawings, the brickwork shall be in composite work with face bricks on the exposed face and balance in standard bricks, but maintaining

the bond fully. Where face bricks are not specified, bricks for the exposed face shall be specially selected from available stack of bricks. All exposed brickwork on completion of work shall be rubbed down, washed clean and pointed as specified. Where face bricks are used, carborundum stone shall be used for rubbing down.

  - Reinforcing anchorage

For external walls, the anchorage in the form of flats or rods from spandrel beams and columns and any other anchoring and reinforcement as shown on the drawing shall be adequately embedded in the masonry.

Table 2: Frequency of sampling and testing

| Sl. No. | Type of material/ work | Nature of test /Characteristics of test | Method of test | No. of samples and frequency | Remarks/ acceptance norms |
| --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 |
| 1. | Burnt clay bricks/Fly ash bricks | (a) Dimensions | Clause No.5.2.1 of IS:1077 |  | Max. 8% deviation for non-modular bricks. For modular bricks as per Clause no.5.2 of IS: 1077. For face bricks as per IS: 2691. |
|  |  | (b) Compressive strength | IS:3495 (Part- 1) |  | As specified |
|  |  | (c) Water absorption | IS:3495 (Part-2) | A set of 20 bricks (min.) for each lot of 50,000 or part thereof for all tests (a to c) | Max. 20%. However, 15% for face bricks only. |
|  |  | (d) Efflorescence | IS:3495 (Part-3) |  | Moderate. However, for face brick nil. |
|  |  | (e) War page | IS:3495 |  | For face brick 2.5 mm (max.) |
| II. | Stone | a) Type of stone by petro graphic | IS:1123 | One set of stones of each | As specified. |
|  |  | examination |  | type and from each source. |  |
|  |  | b) Shape & size | Physical measurement | Random | As specified |
|  |  | c) Crushing strength | IS:1121 (Part-I) | One set of stones of each type and from each source. | As specified |
|  |  | d) Water absorption | IS:1124 | One set of stones of each type and from each source. | As specified |
|  |  | e) Durability | IS:1126 | One set of stones of each type and from each source. | As specified |
| III. | Sand | a) General quality | Visual | One set of samples from each source of material per 100 Cum. or part thereof. | As specified |
|  |  | b) Deleterious material | IS:2386 (Parts-I & 2) | One set of samples from each source of material per 100 cum. or part thereof. | Clause 3.3 of IS:2116 |
|  |  | c) Grading | Sieve analysis as per IS:2386 (Part-I) | One set of samples from each source of material per 100 cum.or part thereof. | Table-1 of IS:2116 |
| IV. | Cement | a) Setting time | IS:4031 | One set of sample for each lot of material received | No separate testing is required in case cement is tested for preparation of concrete mix |
|  |  | b) Compressive strength | IS:4031 | One set of sample for each lot of material received | No separate testing is required in case cement is tested for preparation of concrete mix |
| V. | Water | a) Harmful substances, pH value | IS:3025 | Once a month for each source | No separate testing is required in case water is tested for concrete mix |
|  |  | b) Initial setting time | IS:4031 | Once a month for each source | No separate testing is required in case water is tested for concrete mix |
|  |  | c) Compressive strength | IS:516 | Once a month for each source | No separate testing is required in case water is tested for concrete mix |
| VI. | Mortar | a) Compressive strength | Appendix-A of IS:2250 | One sample (consisting of min 3 specimens) | Table-1 of IS:2250 |
|  |  | b) Consistency | Appendix-B of IS:2250 | One sample for each type of mix | Clause 7.2 of IS:2250 |
|  |  | c) Water retentively | Appendix-C of IS:2250 | One sample for each type of mix | Clause 7.3 of IS:2250 |
| VII. | Masonry construction | a) Workmanship | Visual & Physical measurement | All work | As per specification and Cl. No.11.0 of IS:2212 for brickwork |
|  |  | b) Verticality and alignment | Physical measurement | All work | As per specification and Cl.No.6.3.4 of IS:1905 |

Section - C5

Technical specification for plastering and allied works

# Section - C5

Technical specification for plastering and allied works

Contents

Clause no.	Description

1.	Scope

- General requirements

- Codes and standards

- Materials

- Mortar

- Plastering

- Pointing

# Section - C5: Technical specification for plastering and allied works

- Scope

This part of the specification covers the requirements for plastering and allied works for all types of masonry and concrete surfaces.

- General requirements

  - The Contractor shall furnish all skilled and unskilled labour, plant, equipment, scaffolding, materials, etc. required for complete execution of the work in accordance with the drawings and as described herein and/or as directed by the Engineer.

  - The Contractor shall follow all safety requirements/rules during execution of the work.

  - I.S:1661 shall be followed as a general guidance for plastering work.

- Codes and standards

  - All applicable standards, acts and codes of practice referred to shall be the latest editions including all applicable official amendments and revisions. A complete set of all these documents shall generally be available at Site with the Contractor.

  - In case of any conflict between this specification and those (IS Standards, Codes etc.) referred to in clause 3.3, the former shall prevail.

  - Some of the applicable Indian Standards, Codes, etc. are referred to here below:

IS:383	Coarse and fine aggregates from natural sources for concrete.

IS:712	Building limes.

IS:1542	Specification for sand for plaster

IS:1635	Code of practice for field slaking of Building lime and preparation of putty

IS:2250	Code of practice for preparation and use of masonry mortar. IS:2333	Plaster-of-paris

IS:2402	Code of practice for external rendered finishes

IS:3150	Gypsum building plaster hexagonal wire netting for general purpose

IS:2547 Gypsum building plaster

IS:3150	Hexagonal wire netting for general purpose

- Material

  - Materials namely, cement, sand, water, Coarse aggregate, shall be in accordance with Technical Specifications for properties, storage and handling of common building materials.

  - Lime for preparation of putty or neeru for punning work shall be according to class B& C of IS: 712.

  - For rough cast plaster, coarse aggregate of size 6 to 12 mm shall be used in the finishing coat. Coarse aggregate shall be as per IS: 383.

  - Gypsum, for use in plaster-of-paris punning work shall be according to IS:2333.

  - For lath plastering, galvanised hexagonal wire netting with wire 0.9mm dia and 12.5 mm mesh conforming to IS:3150 shall be used.

- Mortar

  - Unless otherwise specified cement & Fly ash (20% replacement ratio of cement with fly ash): - sand mortar shall be used. Cement mortar shall be prepared by mixing cement & fly ash (20% replacement ratio of cement with fly ash): and sand in specified proportions by volume. Sand shall be measured on the basis of its dry volume using gauge boxes. Suitable allowance in quantity shall be made to cater for the bulkage. Cement and fly ash shall preferably be measured by weight. For the purpose of determining the corresponding volume, one cubic metre of cement shall be taken to weigh 1440 Kg and one cubic metre of fly ash shall be taken to weigh 641 Kg (i.e. coal ash).

  - The mixing of mortars shall be done in mechanical mixer. However, depending on nature, magnitude and location of the work, the Engineer may relax the condition of use of mechanical mixer and allow hand mixing.

Cement, fly ash and sand in the specified proportions shall be fed into the mixer and mixed dry thoroughly in the mixer. Water shall then be added gradually and the wet mixing continued for at least 3 minutes. Hand mixing shall be carried out on a clean, water tight platform. Only that quantity of mortar, which can be used within 30 minutes of its mixing, shall generally be prepared at a time. Care shall be taken, not to add more water than that which shall bring the mortar to the consistency of a stiff paste. IS: 2250 and IS:1661 shall be referred for ascertaining the quantity of water.

In case of cement mortar, the mortar that has stiffened because of evaporation of water from the mortar may be retempered under special circumstances, with the approval of the Engineer, by adding water as frequently as needed to restore the requirements of consistency but this retempering shall be permitted only up to one hour from the time of addition of cement.

Cement mortar shall be used as soon as possible after mixing and before it begins to set, preferably within half an hour from the time water is added to cement during mixing and in any case within one hour thereof.

Sweep mortar shall not be used.

- Plastering

  - Mix proportion and plaster thickness

The mix proportion and thickness of plaster for various surfaces shall be as specified or shown in the drawings. Unless otherwise specified the following shall be adopted.

| i. | Ceiling plaster | minimum 6mm thick cement mortar (1:4) |
| --- | --- | --- |
| ii. | Plaster on external/ rough face of masonry work or concrete surface | 18mm thick, cement mortar* (1:6) |
| iii. | Plaster on plain face of masonry work or concrete surface. | 12mm thick, cement mortar*(1:6) |

*In case of special application like water proofing surface, base course of decorative finish etc., richer mix proportion not leaner than 1:4 shall be used.

  - Preparation of surface

## The surface shall be cleaned of all dust, loose mortar droppings, traces of algae, efflorescence and other foreign matter by water or by brushing. Smooth surfaces shall be roughened by wire brushing, if it is not hard and by hecking when it is hard. In case of concrete surface, if a chemical retarder has been applied to the framework, the surface shall be roughened by wire brushing and all the resulting dust and loose particles cleaned off and care shall be taken that none of the retarders is left on the surface.

## Trimming of projections, wherever necessary shall be done to achieve an even surface. Ranking of joints in case of brickwork where necessary shall be done. The masonry shall be allowed to dry out for sufficient period before plastering.

## For ceiling plaster, the concrete surface shall be pock marked with a pointed tool to ensure a proper key for the plaster.

## The wall shall be dampened evenly and not soaked before application of plaster. If the surface becomes dry in spots, such areas shall be moistened again.

  - Sequence of plastering operations

For external plaster, the plastering operations shall be started from the top and carried downwards. To ensure even thickness and a true surface, plaster about 15 x 15 cm shall be first applied horizontally and vertically, at not more than 2m intervals over the entire surface to serve as gauges. The surfaces of those gauged areas shall be truly in the plane of the finished plastered surface. For internal plaster, the plastering operations may be started wherever the building frame and cladding work are ready; the temporary supports of the ceiling resting on the wall have been removed.

The first undercoat shall then be applied to ceilings. After the ceiling plaster is completed and scaffolding for the same removed, the first undercoat on walls shall then be applied.

After a suitable time, interval as detailed under application of plaster, the second coat (finishing coat) shall be applied, first to the ceiling and then to the walls.

Where corners and edges have to be rounded off, such rounding off shall be completed along with the finishing coat to prevent any joint marks.

  - Application of plaster

    - Wall/vertical surface plaster

Unless otherwise stated, the plastering above 12mm thick shall be carried out in two coats only.

- The backing or first coat

The backing coat shall be 10 to 12 mm thick and carried to the full length of the all or to natural breaking points like doors and windows. Before the rendering coat hardens, it shall be roughened to provide mechanical key for the second coat.

Masonry walls on which plaster is to be applied directly, shall be properly set and cured with the joints raked to a depth of at least 10 mm. The rendering coat shall be troweled hard and tight, forcing it into surface depressions to obtain a permanent bond.

On smooth concrete walls, the surface shall be roughened and the rendering coat shall be dashed on to ensure adequate bond. The dashing of the rendering coat shall be done using a strong whipping motion at right angles to the face of the wall, or it may be applied with a plaster machine or cement gun.

- Finishing coat

Before starting to apply the finishing coat, the surface of the backing coat shall be dampened evenly. The final plastered surface shall be cured and kept continuously damp for minimum 7 days.

  - Trueness of plastering system

The finished plastered surface shall not show any deviation more than 4 mm when checked with a straight edge of 2 metre length placed against the surface.

  - Thickness of plaster

The thickness of the plaster shall be measured exclusive of the thickness of key i.e. grooves or open joints in brickwork. The average thickness of plaster shall not be less than the specified thickness. The minimum thickness over any portion of the surface shall not be less than the specified thickness by more than 3 mm for plaster thickness above 12 mm and 1 mm for ceiling plaster. Extra thickness required in dubbing behind rounding of the corners at junctions of wall or in plastering of masonry cornices etc. shall be ignored.

  - Inspection and testing

- The plastered surface shall be checked for following defects and the remedial measures for the same shall be adopted as per IS: 1661.

  - Blistering

  - Bound failure or loss of adhesion

  - Cracking

  - Crazing

  - Efflorescence

  - Grinning

  - Irregularity of surface texture

  - Popping or blowing

  - Recurrent surface dampness

  - Softness or chalkiness

- Trueness of the plaster shall be checked as per Clause no. 6.6

- Thickness of the plaster shall be checked as per Clause no. 6.7

Water supply and sewer (WS) works

Sub-Section - WS - 1

Technical specifications for laying of pipes and fittings / specials

## Sub-Section - WS - 1

Technical specifications for laying of pipes and fittings / specials

## Contents

Clause no.			Description

- Scope

- Applicable codes

- Carting & handling

- Storage

- Laying

- Measurement

- Notes

# Sub-Section - WS - 1: Technical specifications for laying of pipes and fittings / specials

- Scope

The work shall include providing of materials (Pipes alone will be supplied free of cost at site by the Employer), all necessary plant and equipment, providing adequate engineering supervision and technical personnel, skilled and unskilled labour, etc. as required to carry out the entire work as indicated on the drawings and/or described herein subsequently and/or as directed by the Engineer. The Contractor shall carry out all works meant within the intent of this specification even if not explicitly mentioned herein.

All works shall be executed to the satisfaction of the Engineer.

This specification is divided into 5 sections, sections C-1, C-2, C-3, C-4 & C-5 deal with specifications for 5 different items / activities for civil construction items which will be met with during laying of the pipelines. All these five sections are as follows: -

| Section C - 1 | Technical specification for Excavation and Filling. |
| --- | --- |
| Section C - 2 | Technical specification for properties, storage and handling of common building materials |
| Section C - 3 | Technical specification for cast in situ concrete and allied works |
|  | Sub section: |
|  | 1. Common requirement |
|  | 2. Cast in situ concrete and Allied works. |
|  | 3. Reinforcement |
|  | 4. Form work and staging |
| Section C - 4 | Technical specification for masonry and allied works. |
| Section C - 5 | Technical specification for plastering and allied works |

The two parts (i.e. Specifications from C-1 to C-5 as mentioned above are complementary and are to be read together for a correct interpretation of the provisions of this specification.

- Applicable codes

The laying of pipes and fittings/specials shall comply with all currently applicable statutes, regulations, standards and codes. In particular, the following standards, unless otherwise specified herein, shall be referred. In all cases, the latest revision of the standards/codes shall be referred to. If requirements of this specification conflicts with the requirements of the standards/codes, this specification shall govern.

Any approval, instructions, permissions, checking, review, etc. whatsoever by the Engineer, shall not relieve the Contractor of his responsibility and obligation regarding adequacy, correctness, completeness, timely completion, safety, strength, quality & workmanship etc.

The Contractor shall make his own surveying arrangements for locating the coordinates and positions of all work and establish the reduced levels (RLs) at these locations, based on two reference grid lines and one bench mark which will be furnished by the Employer. If need be the Employer reserves the right to have the Contractor re-verify the coordinates at no cost to the Employer. The Contractor has to provide at site, all the required survey instruments, along with qualified surveyors, to the satisfaction of the Engineer so that the work can be carried out accurately and according to the specifications and drawings.

  - Codes of practice

All applicable standards, specifications, etc. and codes of practice shall be the latest editions, including all applicable official amendments and revisions. A complete set of all these documents shall generally be available at site, with the Contractor.

All work shall be carried out as per the stipulations contained in various sections of these specifications and the latest Indian Standards, Act, Codes and best practices.

In case of conflict between the stipulations contained in various sections of these specifications and stipulations of Indian Standard Codes, etc. the requirements of stipulations contained in various sections of these specifications shall prevail over that of Indian Standards, Codes, etc. Contractor is responsible to notify the Employer in writing well in advance of such conflicts prior to execution of the work.

Some of the applicable Indian Standards, Codes are referred to herein below:

| a) | IS.783 | Code of practice for laying of concrete pipes |
| --- | --- | --- |
| b) | I.S. 3764 | Excavation work - code of safety |
| c) | I.S. 5822 | Code of practice for laying of electrically welded steel pipes for water supply |
| d) | I.S. 1726 | Specifications for Cast Iron Manhole covers & frames |
| e) | I.S. 5455 | Specifications for C.I. steps for manholes. |
| f) | I.S.4111 | Code of practice for ancillary structures in sewerage system (Part - 1) (manholes) |
| g) | I.S.12288 | Code of practice for use and laying of D.I. Pipes |
| h) | IS 1200 part16 | Method of measurement of building and civil engineering works: Laying of water and sewer lines including appurtenant items |
| i) | IS 7634 | Code of practice for plastics pipe work for potable water supplies: |
|  |  | Part 1 - Choice of materials and general |

|  |  | Part 2 - Laying and jointing of polyethylene (PE) pipes |
| --- | --- | --- |
|  |  | Part 3 - Laying and jointing of UPVC pipes |
| j) | IS 12235 (Parts 1 to 19) | Thermoplastics pipes and fitting - methods of test |
| k) | IS 15328 - 2003 | Un plasticized Non-Pressure Polyvinyl Chloride (PVC-U) Pipes for use in Underground Drainage and Sewerage Systems |
| l) | IS 4985 -2000 | Un plasticized PVC Pipes for Potable Water Supplies |

The above codes are only indicative. Any other codes relevant to the works concerned shall be applicable for specifications.

- Carting & handling

Pipes and fittings/specials shall be transported to all the work sites at places along the alignment of pipeline as directed by the Employer/Engineer. Contractor shall be responsible for the safety of pipes and fittings/specials in transit, loading/unloading storage etc. Every care shall be exercised in handling pipes and fittings/specials to avoid possible damage. While unloading, the pipes and fittings/specials shall not be dropped down from the truck on to any hard surfaces. They should be unloaded on timber skids with steadying ropes or by any other approved means. Padding shall be provided between coated pipes, fittings/specials and timber skids to avoid damage to the coating. Suitable gaps between pipes/stacks of pipe should be left at intervals in order to permit free access from one side to the other. In case of spigot & socket pipes care should be taken regarding orientation of pipes while unloading. As far as possible pipes shall be unloaded on one side of the trench only the pipes shall be checked for any visible damage (such as broken edges, cracking & spalling of pipe etc.) while unloading and shall be sorted out for replacement. Any pipe which shows any damage to preclude it from being used shall be discarded. Dragging of pipes and fittings/specials along concrete and similar pavement with hard surfaces shall be prohibited.

- Storage

  - Each stack of pipes shall contain only pipes of same class and size, with consignment or batch number marked on it with particulars of suppliers wherever possible. Storage shall be done on firm level and clean ground and wedges shall be provided at the bottom layer to keep the stack stable. The stack shall be in pyramid shape or the pipes laid lengthwise and crosswise in alternate layers. The pyramid stack shall be made for smaller diameter pipes for conserving space in storing them. The height of the stack shall not exceed 1.5 m. Also necessary security arrangements should be provided to avoid these till the pipes are finally used.

  - Fittings/specials shall be stacked under cover and separated from pipes and with suitable security measures.

  - Rubber rings shall be stored in a clean & cool store away from windows, boiler, electrical equipment and petrol, oils or other chemicals. Particularly in the field where the rubber rings are being used it is desirable that they do not be left out on the ground in the sun or overnight under heavy frost or snow conditions.

- Laying

  - General

The Contractor shall visit the site before tendering and get himself acquainted with site conditions and the regulations regarding the laying of pipes in congested areas, heavy traffic areas etc. The successful bidder shall obtain necessary permissions and clearances from all the local authorities, department of roads, traffic, water supply and drainage, electricity board, telephone company etc. wherever necessary.

Road reinstatement shall not be included in backfilling unless specified.

General lighting for worksite, warning lights, sign boards, fencing & barricading etc. shall be provided by Contractor at his own cost.

  - Excavation

    - Before excavating the trench the alignment of pipeline shall be approved by the Employer/Engineer. The excavation of trenches and pits for manholes/chambers shall be carried out in accordance with the specifications contained herein below and shall be done in such a manner that IT DOES NOT GET FAR AHEAD OF THE LAYING OPERATION as approved by the Employer/Engineer.

After excavation of trenches, pipes shall not be lowered in position unless the dimensions of trenches and bedding work at the bottom of the trenches are-approved and measured by Engineer / the Employer. Pipes and fittings shall be carefully lowered in the trenches. Special arrangements such as cranes, tripods with chain pulley block etc. for lowering the pipes and fittings shall be made by Contractor at his own cost. In no case pipes shall be dropped. Slings of canvas or equally NON ABRASIVE MATERIAL of suitable width and strength or special attachment to fit the ends of pipes and fittings shall be used to lift and lower the coated pipes and fittings. The pipes and fittings shall be inspected for defects and, be struck with light hammer preferably while in suspended position to detect presence of any cracks. If doubt persists, further confirmation shall be done by pouring a little Paraffin on the inside of the pipe at the suspected spot and after doing vigilant investigation whether the Paraffin is leaking on to the external side of the pipe or not then only the non leaking pipe should be considered fit for use. Pipes and fittings damaged during lowering or aligning shall be replaced by contractor at no extra cost.

    - To protect the persons from injury and to avoid any damage to property, adequate barricades, construction signs, red lanterns and guards, as required for smooth functioning of work and to avoid any minor or major accidents, shall be placed and maintained during the progress of the construction work and until it is safe for the traffic to use the roadways. The relevant Indian Standards and the rules and regulations of local authorities in regard to safety provisions shall be observed.

    - Suitable fencing/barricades shall be provided along the sides of trenches and pits. The posts of fencing shall be of timber securely fixed in the ground not more than 3m. Apart and they shall not be less than 75 mm. in diameter or less than 1.2 m. above the surface of the ground. There shall be two rails, one near the top of the posts and the other about 450 mm. above the ground and each shall be from 50 mm. to 70 mm. in diameter and sufficiently long to run from post to post to which they shall be bound with strong rope. The method of projecting rails beyond the posts and tying them together where they meet will not be allowed on any account. All along the edges of the excavated trenches a bund of earth about 1.2 m. high shall be formed where required by the Employer/Engineer (but due care shall be taken while stacking the excavated stuff to cause least inconvenience for day to day site activities) for further protection. The above work shall not be paid for separately and the Contractor shaft takes into account the costs of such works and quote accordingly.

Total quantity of water required for entire work including for testing- pipes and fittings at work site shall be arranged by Contractor at his own cost. Dragging of pipes and fittings along concrete and similar pavements with hard surfaces shall be prohibited.

    - The road metal and also the rubble packing obtained out of road surface excavations etc shall first be stripped off for the whole width and entire length of the trench/pit and separately deposited in such place or places as may be determined by the Employer/Engineer. In case of the metal packing or "Khandkies" not being so deposited or being mixed up with excavated materials and not available for backfilling and making good the excavation, the cost of the new metal, packing or "Khandkies" required shall be charged to the Contractor.

    - The portions of trenches in stony or rocky ground are to be excavated all along to the entire length and for the full depth such that the bottom of the excavation shall not be higher at any point than the bottom of the concrete' bedding layer below the sewer pipe.

During excavation, large stones and rubble shall be separated and removed from the excavated soil and stacked separately. The material from excavation shall be deposited on either side of the trench leaving adequate clear distance from the edges of the trench and pit or as may be necessary to prevent the sides of the trench/pit to "cave-in" or at such a distance and in such a manner as to avoid covering fire hydrants, sluice valves, manhole covers etc., and so as to avoid abutting the wall or structure or

causing inconvenience to the public and other service, organization or otherwise as the Employer/ Engineer may direct.

    - Contractor also shall take into account while quoting his rates for possible additional excavations for trial pits of such sizes and depths that may be required to be undertaken by him as per the instructions of the Employer/Engineer for determining the locations of various existing underground service line such as water pipes, drains, sewers, gas pipelines, electric and telephone cable etc. which may be met with. Contractor should also as per the instructions of the Employer/Engineer backfill and thoroughly compact all such additional excavations and make the area as original after the purpose of locating is served. No additional payment will be considered by the Employer on this account.

During the pendency of the contract the Contractor should take all due precautions for proper maintenance and protection against damage of all such service lines if met with during excavation, by means of shoring, strutting, planking over, padding- or otherwise as the Employer / Engineer may direct. Also all precautions shall be taken during excavation and laying operations to guard against possible damage to any existing structures. In case if any such damages have occurred then those shall be made good either by Contractor or by other agency, as Engineer/the Employer may decide and wholly in either case at the expense of Contractor.

    - If the work for which the excavation has been made is not completed by the expected date of the setting of monsoon or the setting in of rain whichever is earlier, or before the day fixed by the Employer/Engineer for filling in any excavation on account of any festival or special occasion, contractor shall backfill such excavation and consolidate the filling at his own expenses as directed by Engineer/the Employer and shall re- excavate when required at his own cost.

Engineer/the Employer may order portions of shoring to be left in the trenches at such places, where it is found absolutely necessary to do so as to avoid any damage which may be caused (because of pulling out shoring from the- excavated trench/pit) to buildings, cables, gas mains, water mains, sewers etc. in close proximity of the excavation. Contractor shall be paid at the negotiated rate for the shoring left in the trenches / pit if directed by Engineer / the Employer. Contractor shall not claim, for any reasons whatsoever for the shoring which may have been left in position by him at his own discretion. Contractor shall not be paid for shoring left in the portions of the rakers, struts, or other timber cut off and not permanently left in the work.

    - Utmost care shall be taken to see that the width of the trench at the top of pipe is not more than that as specified. In case additional width is required it shall be provided only in the top portion from the ground level up to 300 mm. above the crown of pipe. If any extra width is provided in the area below this portion because of mistake on part of the Contractor, Contractor shall have to provide remedial measures in the form of lime concrete or rubble masonry or otherwise at the discussion and to the satisfaction

of the Employer / Engineer. Contractor shall not be paid any additional for extra excavation as well as for the resulting remedial measures adopted to make up for the additionally done excavation. If rock is met with, it shall be removed to 15 cm. below the bottom of pipes and fittings / specials and the space resulting shall be refilled with granular materials and properly consolidated. No compensation will be paid to the Contractor on this account and financial implications for the same should be included by the Contractor in his rates. Bottom of trenches / pits shall be saturated with water and well rammed wherever the Employer / Engineer may consider it necessary to do so.

    - Wherever a socket or collar of pipe or fitting / special is to be accommodated a strip sufficient enough for this purpose is to be cut in the bottom of the trench or concrete bed to a depth of at least 75 mm. below the bed of the pipe so that the pipe may have a fair bearing on its shaft and does not rest upon its socket. Such strip shall be of sufficient size in every respect to admit the free movements of hand holding necessary tools of the skilled worker, all around the socket in order to make the joint completely watertight and the strip shall be maintained clear until the joint has been approved by the Employer / Engineer.

All the pipes are to be laid perfectly true both in alignment and to the gradient specified.

    - When welding is to be carried out with the pipes and specials in the trench, additional excavation of not more than 60 cm. in depth and 90 cm. in length shall be made at joints in order to facilitate welding. The excess volume of this excavation should be brought to the acceptable level by making good with necessary fill material as directed by the Employer / Engineer. The charges on this account should be included in his rates by the Contractor.

    - The excess excavated material shall be carried away from site of works to a place up to a distance as directed by the Employer / Engineer. This shall be done immediately so as not to cause any inconvenience to the public or traffic. If the instructions from Engineer are not implemented within seven- days from the date pf instructions to cart the materials and to clear the site, the same shall be 'carried out by the Employer/Engineer at the risk and cost of the Contractor and any claim or dispute shall not be entertained in this respect.

  - Dewatering

    - During the excavation, if subsoil water or water mixed with- day/slush- is met with Contractor shall have to provide necessary equipment and labourers for dewatering the trenches/pits by bailing out water or clay/slush; if pumping out subsoil water is found to be necessary, Contractor shall provide pumps in sufficient numbers/type for the same. In both the above cases the excavation shall be done to the required level and the pipes shall be laid to proper alignment and gradient. Contractor shall also make foolproof necessary arrangement for the disposal of drained water to nearby

storm water drain or in a pit if allowed by the Employer/Engineer. In no case the water shall be allowed to- spread indiscriminately over the adjoining area. Before discharging this water into public sewer/drain, Contractor shall take necessary permission from all the local authorities before implementing the draining arrangements.

  - Special foundation in poor quality soil

    - Where the bottom of the trench at subgrade is found to consist of material which is unstable to such a degree that in the opinion of the Employer/Engineer, it cannot be removed and replaced with an approved material thoroughly compacted in place to support the pipe properly, a suitable foundation for the pipes, consisting of piling, timbers or other materials, in accordance with relevant drawings and as instructed and approved by the Employer/Engineer shall be constructed.

    - When the work of constructing the pipelines has to be carried out in soft underground strata, such as puddle etc. or in a reclaimed land, a good foundation shall be provided for the pipes and manholes. For the former, excavation in the trench shall be taken 75 mm. deeper than what is ordinarily required and for this depth the whole of the trench shall be covered over with M-150 bed concrete of the required width, reinforced with B.R.C. fabric No.9 or any other fabric- approved-by the Engineer.

    - The fabric shall be suitably cut to the requirement and securely joined together with adequate laps which should not be less than 200 mm. The fabric in the pipeline must also be securely jointed together. The rates in both the cases shall beheld to include all lapping, jointing and also any probable wastage.

  - Wooden shoring

    - Contractor shall suitably design polling boards, walling and struts to meet different soil conditions that might be encountered in excavating trenches/pits. The horizontal and vertical spacing of struts shall, be such that not only the sides of trenches shall be prevented from collapse but also easy lowering of pipe in trenches shall be ensured without creating undue obstructions for the excavation of the work. Any inconvenience and/or delay that might be caused in lowering pipes in trenches as a result of adopting improper spacing of struts by Contractor shall be his sole responsibility. No part of shoring shall at any time be removed by Contractor without obtaining permission from the Employer/Engineer. While taking out shoring planks the hollows of any form must simultaneously be filled in with soft earth well-watered & rammed with rammers.

    - The Employer/Engineer may order portions of shoring to be left in the trenches/pits at such places, where it is found absolutely necessary to do so as to avoid any damage which may be caused to the adjacent buildings, cables, gas-mains, water mains, sewers etc. in close proximity of the excavation, by pulling out the shoring from the excavations. Contractor shall not claim, on any reason, whatsoever for the shoring which may have been left in by him at his own discretion.

  - 5teel plate shoring

    - Where the subsoil conditions are expected to be of a soft and unstable character in trench/pit excavation the normal method of timbering may prove insufficient to avoid subsidence of the adjoining road surfaces and other services. In such circumstances contractor will be required to use steel trench sheeting or sheet piling adequately supported by timber struts, walling etc., as per the instructions, manner and method directed by the Employer/Engineer. Contractor shall supply, pitch drive and subsequently remove trench sheeting or piling in accordance with other items of the specification.

  - Boning staves and side rails

    - In laying the pipes and fittings/specials the centre for each pipeline shall be marked by a peg. Contractor shall dig holes for and set up two posts (about 100 mm. x 100 mm. x 1800 mm.) at each junction of pipelines at nearly equal distance from the peg and at sufficient distances there from to be well clear of all intended excavation, so arranged that a side rail when fixed at a certain level against the post shall cross the centre line of the manhole / chamber or pipelines. The side rail shall not in any case be more than 30 m. Apart intermediate rails shall be put up if directed by the Employer / Engineer.

    - Boning staves of 75 mm. x 50 mm. size shall be prepared by Contractor in various lengths, each length being of a certain whole number of metres and with a fixed tee- head and fixed intermediate cross pieces, each about 300 mm. long. The top-edge of the cross piece must be fixed below the top-edge of this tee-head at a distance equal to the outside diameter of the pipe or the thickness of the concrete bed to be laid as the case may be. The top of cross pieces shall indicate different levels such as excavation for pipeline, top of concrete bed, top of pipe etc. as the case may be.

    - The side rail of size 250 mm. x 40mm. shall be screwed with the top edge resting against the level marks. The centre line of the pipe shall be marked on the rail and this mark shall denote also the meeting point of the centre lines of any converging pipes. A line drawn from the top edge of one rail to the top edge of the next rail shall be vertically parallel with the bed of the pipe and the depth of the bed of pipe at any intermediate point may be determined by letting down the selected boning staff until the tee head comes in the line of the sight from rail to rail.

    - The post and rails shall be perfectly square and planed smooth on all sides and edges. The rails shall be painted white on both sides, and the tee heads and cross piece of the boning staves shall be painted black.

    - For the pipes converging to a manhole / chamber at various levels, there shall be a rail fixed for every different level. When a rail comes within 0.60 M. of the surface of the ground, a higher sight rail shall be fixed for use with the rail over the next point.

    - The posts and rails shall be in no case be removed until the trench is excavated, the pipes are laid and the Employer / Engineer gives permission to proceed with the backfilling.

  - Encasing / being / hunching etc.

    - The pipes shall be provided with encasement / bedding / hunching etc. as specified in drawings.

  - Laying of pipes and fittings / specials

    - All precautions shall be taken during excavation and laying operations to guard against possible damage to any existing structure / pipeline of water, gas, sewage etc. and excavation to proceed in accordance with the stipulations of Clause No. 5.2.1 of this specifications.

    - All the pipes are to be laid perfectly true both in alignment and to gradient specified In case of spigot and socket pipe the socket end of the pipe shall face upstream EXCEPT WHEN THE PIPELINE RUNS UPHILL IN WHICH CASE THE SOCKET ENDS SHOULD FACE THE UPGRADE. The laying of pipes shall always proceed upgrade of a slope. After placing a pipe in the trench, the spigot end shall be centered in the socket and the pipe forced home and aligned to required gradient. The pipes shall be secured in place with approved backfill material tamped under it except at the socket. Pipes and fittings / specials which do not allow a sufficient and uniform space for joints shall be removed and replaced with pipes and fittings / specials of proper dimensions to ensure such uniform space: Precaution shall be taken to prevent dirt from entering the jointing space. At times when pipe laying is not in progress, the open ends of pipe shall be closed by a watertight plug or other means approved by the Employer / Engineer. During the period that the plug is on, the contractor shall take proper precautions against flotation of the pipe owing to entry of water into the trench: Wherever it is necessary to deflect pipe from a straight line, either in the vertical or horizontal plane, to avoid obstructions or where long radius curves are permitted, the deflection allowed at joints shall not exceed 21 /2°. In the case of pipes, with joint to be made with loose collars, the collars shall be slipped on before the next pipe is laid. The pipes shall be laid such that the marking on pipes appears at the top of the pipes.

    - The cutting of pipe for inserting valves, fittings or closure pieces /specials shall be done in a neat and workmanlike manner without damage to the pipe so as to leave a smooth end at right angles to the axis of the pipe. For this purpose, pipe cutting machine shall be used and skilled labourers only should be allowed to achieve this task.

  - Thrust blocks

    - Thrust blocks shall be provided as directed by the Employer / Engineer to counteract hydraulic thrust, at places wherever directed and as per relevant drawing.

    - Where the hydraulic thrust is in an upward direction, anchor blocks as per the relevant drawing shall be provided to which the pipes shall be secured with steel straps.

  - Jointing of pipes

    - Jointing for pipes and fittings / specials shall be done in accordance with: the relevant specifications depending on type of pipes being used. (Please refer Clause No.2.1 of these specifications)

  - Testing and commissioning

    - Testing and commissioning of pipes shall be done in accordance with the relevant specifications.

  - Backfilling

    - Trenches shall be backfilled with approved selected excavated material only after the successful testing of the pipeline. The tamping around the pipe shall be done by hand or other hand operated mechanical means. The water content of the soil shall be as near the optimum moisture content as possible. Filling of the trench shall be carried out simultaneously on both sides of the pipe in such a manner that the level of filling rises gradually and unequal pressure does not occur on the pipe. Back filling shall be done in layers not exceeding 30 cm. Each layer shall be consolidated by watering, ramming, care being taken not to damage to the pipeline. In case of mild steel pipes / specials, the spiders provided during assembly and welding shall be retained until the trench is refilled and consolidated. Where timbers are placed under the pipeline to aid alignment, these timbers shall be removed before backfilling.

  - Reinstatement of road / footpath

    - Reinstatement of road / footpath shall be done as per requirements of local authorities and the relevant specifications after the completion of work.

  - Clearing of site

    - All surplus materials, and all tools and temporary structures shall be removed from the site as directed by the Employer / Engineer and the construction site left clean to the satisfaction of the Employer/Engineer.

- Measurement

  - The measurements for excavation in trenches shall be done in following manner and will be paid accordingly.

- Length (L)	As per the actual length of pipe and fittings / specials laid      at work site.

Width (B)	Average width as per the standards specified in the Central Public Works Department, Government of India for water supply works.

- Depth (D)	Average depth of trench from natural ground level to bottom of pipe or fittings.

  - Excavation of asphalt road and reinstatement of road shall be measured on per square meter basis and the length and width at top of trench shall be considered same as those mentioned for excavation of trench.

The rate for this item should be inclusive of all excess excavated material to be transported from site of work to a place up to a maximum distance of 5 km. as directed by Engineer / the Employer immediately after his instructions so as not to cause any inconvenience to the public or traffic.

  - In case the excavation is done in wet condition either by bailing out water or by resorting to pumping, the respective items shall be paid according to the items in schedule of quantities and rates. The measurement for these items shall be made as per the units for relevant item(s) in schedule of quantities and rates. However, Engineer will decide on site the mode of dewatering and his decision shall be final and binding on Contractor.

  - Shoring (open / close) if to be paid separately shall be measured on the square metre basis of the actual area of trenches shored.

  - The measurement for removal of excess excavated material up to a specified distance shall be as per the relevant item(s) in the Schedule of Quantities and Rates and shall be measured on cubic metre basis. In case of soil 30% deduction shall be done to take account for voids whereas it will be 40% in case of rubble.

  - Measurement for pipes and fittings / specials shall be in accordance with the relevant clause(s) of specification for particular type of pipes.

- Notes

  - Fencing provided along the sides of trenches and pits shall not be paid for separately and Contractor shall take into account the costs of such works and quote accordingly.

  - In case of the road metal packing or dressed stones not being deposited as specified or being mixed up with excavated materials and not available for the reinstatement of road / pavement, the cost of the new metal packing or dressed stones required shall be charged to Contractor by the Employer / Engineer.

  - Service lines if damaged during excavation shall be made good either by Contractor or by other agency as the Employer / Engineer may decide and wholly in either case at the expense of Contractor.

  - Contractor shall not be paid any additional compensation for excess excavation over what is specified as well as for any remedial measures that are specified.

  - The excess excavated material shall be carried away from site of works as specified, failing which in view of public safety and traffic convenience the Employer / Engineer may carry out the work by any other agency at Contractor's risk and cost.

  - Portion of shoring left in the excavated trenches or pits shall be measured and paid separately, if instructed by the Employer / Engineer to do so.

Sub-Section - WS - 3

Technical specifications for laying and jointing of ductile iron fittings

## Sub-Section - WS - 3

Technical specifications for laying and jointing of ductile iron pipes and fittings

Contents

Clause no.	Description

- Scope

- Applicable codes

- Laying

- Valves

- Jointing

- Measurement

- Notes

# Sub-Section - WS - 3: Technical specifications for laying and jointing of Ductile Iron pipes and fittings

- Scope

This specification covers the requirements for collecting, transporting to work sites, laying, jointing and field testing of ductile iron pipes (Pipes will be supplied free of cost at site by the Employer) and fittings for the water distribution and transmission Network.

- Applicable codes

Various operations such as transporting to work sites, lowering in trenches, laying, jointing and field testing of ductile iron pipes and fittings shall comply with all currently applicable standards. In particular, the following standards, unless otherwise specified herein, shall be referred. In all cases, the latest revision of the standards shall be referred to. If requirements of this specification conflict with the requirements of the standards, this specification shall govern.

- Ductile Iron Pipes - K7/K9 Class- IS : 8329

- Specials (Tees, crosses, bends etc. - IS: 9523

- Property connections & Fittings - IS : 1239 (Part I & II)

- Laying of D.I. pipes - IS: 12288

- Sluice Valves - IS : 14846/2000

- Butterfly Valves (Double flanged long body) - BS : 5155 / IS: 13095

- Kinetic Double Air Valves with isolating sluice valve - IS: 14845/2000

- Fire Hydrants-IS : 908

- Rubber Gasket for Flanged Connection - IS : 638

- Ferrules - IS : 2692

- Specification for rubber sealing rings for gas mains, water mains and sewers. IS::5382

- Scour valve including D.I. K7/K9 class drain pipe of dia. equivalent to that of Scour valve and 6 m. length IS:780 & IS:2906

- Laying

For Clauses No.3.0 i.e. Carting and Handling, 4.0 i.e. Storage and 5.0 i.e. Laying

- please refer Sub-Section WS-1 for "Technical Specifications for Laying of Pipes and Fittings / Specials" which are common for this item also.

- Valves

  - General

- Valves shall be as per internationally recognized standards. Flanges shall be machined on faces and edges and conform  to ISO 7005, IS 6392 or BS 4504.

- Valves shall be double flanged type and the face shall be parallel to each other and flange face should be at right angles to the valve centerline. Back side of valve flanges shall be machined or spot faced for proper seating of the head and nut.

- Valve buried or installed in underground chamber, where access to a hand wheel would be impractical shall be operated by means of extension spindle and / or keys.

- Valve of diameter 450 mm. and above shall be provided with lifting eyes and shall have detachable bolted covers for inspection, cleaning and servicing.

- Valve shall be suitable for frequent operation as well as operation after long periods of idleness in either open or closed position.

- The valve stem, thrust washers, screws, nuts and all other components exposed to the water shall be of a corrosion resistant grade of stainless steel.

- Valves shall be free from sharp projections.

  - Butterfly valves

- Butterfly valve shall be as per IS 13095 / BS 5155. Valve shall suitable for mounting in any position.

- The valve seat shall be secured to the valve body. When the valve is fully closed, a seal shall seat firmly so as to prevent leakage. The seat surfaces shall be machined smooth to provide a long life for the seal.

- The valve seal shall be replaceable and securely clamped to the edge of the disc by stainless steel seal retention members, or equivalent so as to prevent leakage and to hold the seal securely during operation. The seal retention member shall be securely clamped with stainless steel fasteners. All fasteners shall be set flush so as to offer the least resistance possible to the flow-through the valve.

- Valve shall be suitable for throttling purpose.

- All valve spindles and hand wheels shall be positioned to give good access for operational personnel.

- Valve of diameter 450 mm. and above shall be provided with enclosed gear arrangement for ease of operation. The operation gear shall be such that they can be opened and closed by one man against an unbalanced head 15% in excess of the maximum specified rating. Valve and any gearing shall be such as to permit manual operation in a reasonable time and not exceed a required rim pull of 400 N.

- All hand wheels shall be arranged to turn in a clockwise direction to close the valve, the direction of rotation for opening and closing being indicated on the hand wheels

  - Sluice valves

- Sluice valve shall conform to IS 14846/2000 or relevant internationally recognized standards.

- They shall be of rising or non-rising spindle type depending on application. The valve shall be furnished with a bushing arrangement for replacement of packing without leakage. They shall also have renewable channel and shoe linings. The gap between the shoe and channel shall be limited to 1.5 mm.

- The gate face rings shall be screwed into the gate or alternatively securely pegged over the full circumference.

- Valves of 450 mm. and above shall be provided with thrust bearing arrangement for ease of operation.

- Valves of diameter 450 mm. and above shall be provided with enclosed gear arrangement for ease of operation. The operation gear of all valves shall be such that they can be opened and closed by one man against an unbalanced head 15% in excess of the maximum specified rating. Valve and any gearing shall be such as to permit manual operation in a reasonable time and not exceed a required rim pull of 400 N.

- Valves, spindles and hand wheels shall be positioned to give good access for operational personnel.

- All hand wheels shall be arranged to turn in a clockwise direction to close the valve, the direction to close the valve, the direction of rotation for opening and closing being indicated on the hand wheels.

  - Non-return valve

    - The valve shall be suitable for mounting on a horizontal pipeline and flow direction shall be clearly embossed on the valve body.

    - The valves shall possess high speed closing characteristics and be designed for minimum slam condition when closing.

    - In case of multi door swing type check valve, the non-slam characteristic shall be achieved by providing suitable combination of door and hydraulic passages without any external damping arrangements or passages. The angle of sealing and door weight shall be designed to provide the most efficient working with least restriction to flow.

    - Valve of diameter greater than 450 mm. and above shall be provided, with feet and jacking screws in addition to others. Hinge pins / shaft shall preferably be square in section to ensure positive location of flaps and provide for secure fixing.

  - Air valves

    - The valve shall be capable of exhausting air form pipe work automatically when being filled. The air being released at a sufficiently high rate to prevent the restriction of the inflow rate. Similarly, the valve shall be capable of ventilating pipe work automatically when being emptied, the air inflow rate being sufficiently high to prevent the development of a vacuum in the pipelines. The valve shall also automatically release air accumulating in pipe work during normal working conditions.

    - Air valve shall be of the double orifice type with a large orifice for ventilation or exhaust of the pipeline and smaller orifice for automatic release of air under normal working pressure.

    - Air valve shall be designed to prevent premature closure prior to all air having been discharged from the line. The orifice shall be positively sealed in the closed position but the float (ball) shall only be raised by the liquid and not by a mixture of air and liquid spray. The seating shall be designed to prevent the floats sticking after long periods in the closed position.

  - Pressure relief valves

    - Pressure relief valves shall be capable of relieving pressure in the system to prevent the system being pressurized in excess of a preset maximum allowable pressure. The valves shall be drop tight under normal operating conditions.

    - The valve operation shall be achieved by the interaction of the inlet pressure and an intermediate pressure produced by a pilot valve or relay system acting on the upper side of the main valves.

    - The pilot valve or relay system shall be actuated by a diaphragm connected to the inlet pressure on its underside and a constant pressure on its upper side derived either from weight or from a spring.

- Jointing

  - Flexible joint

The spigot and socket flexible joint should be designed to permit angular deflection in direction and axial movement to compensate for ground movement and thermal expansion and contraction. They incorporate gasket of elastomeric materials and the joints may be of the simple push-on-type or the type where the seal is effected by the compression of a rubber gasket between a seating on the inside of the socket and the external surface of spigot. Joints of the latter type are referred to as mechanical joints. Both push-in and mechanical joints are flexible joints. Flexible joints require to be externally anchored at all changes in direction such as at bends, etc. and at blank end to resist the thrust created by internal pressure and to prevent the withdrawal of spigots.

  - Flanged joint

Flanged joints are made on pipes having a machined flange at each end of the pipe. The seal is usually effected by means of a flat rubber gasket compressed between two flanges by means of bolts which also served to connect the pipe rigidly. Gaskets of other materials, both metallic and non-metallic are used for special applications.

  - Joints

    - Proposed jointing of D.I. pipes

It is proposed to use spigot and socket pipes with flexible joints and flanged joints for valves and other appurtenances.

The pipeline shall be laid such that the socket ends should face the upstream on level ground. When the line runs uphill the socket end should face the upgrade.

Whenever valve or hydrant connection is to be made socket and flanged specials or T specials as shown in the drawings shall be used.

In case of rubber ring joints, the groove and the socket shall be thoroughly cleaned before inserting the rubber gasket. While inserting the gasket, it shall be made sure that it takes the proper direction and that it is correctly seated in the groove. After cleaning dirt or foreign materials from the plain end, lubricant shall be applied in accordance with the pipe manufacturer's recommendations. The plain end of the pipe shall be pushed into the socket of the pipe and while pushing, the pipe shall be kept straight. If any deflections are to be made in the alignment, it may be made after the joint is assembled.

For joints between pipe and valve, socket and flanged specials shall be used. The gasket used between flanges of valves and pipe shall be compressed fibre board or natural / synthetic rubber (IS:63S) of thickness between 1.5 to 3.0 mm. The fibre board shall be impregnated with chemically neutral mineral oil and shall have a smooth and hard surface. Its weight per square meter shall be not less than  112 g/mm thickness. Each bolt should be tightened a little at a time taking care to tighten diametrically opposite bolts alternatively. The practice of fully tightening the bolts one after another is highly undesirable.

    - Property connections

A property connection should consist of following parts

      - Brass ferrule

      - Communication pipes with couplings, bends, elbows, union etc. (Length as per drawings)

      - Cap at the end of the communication pipe near the plot boundary.

The plot owner is expected to construct and connect the remaining portion of property connections at plot boundary. The desired arrangement of property connection is shown in Drawing.

    - Connection at main

Boring on water main should be done on top of main to reduce possible entry of silt into pipe and subsequently damaging of meters. A manual drilling and tapping machine should be used for this purpose. A bore shall be drilled and tapped on CI main and a ferrule shall be screwed directly into the bore. Upto 38 mm size of property connections, ferrules shall be used whereas for higher size property connections, T connection shall be given. Ferrule shall be of gunmetal or brass as per IS: 2692. The ferrule should be so set in the main that the communication pipe leads off in line with the main before curving round right handed into its proper course as show in Drawing No. 5-A-I0 . G I. Pipes to be used as property connections shall confirm to IS: 1239. Class C. the pipe should be provided, external protection of bitumen coating with hession cloth wrapped over it. It should be provided with PVC sheathing wherever they are exposed such as in case of drain crossings.

The specials to be used at crossing of pipelines, T joints, 90 deg. bends and valve joints are shown in the Drawing.

  - Testing

After the pipes and specials are laid, jointed and the trench partially back filled except at the joints the stretch of pipeline as directed by Engineer shall be subjected to pressure test and leakage test. Where any section of the rising main is provided with concrete thrust blocks or anchorages, the pressure test shall not be made until at least five days have elapsed after the concrete was cast. If rapid hardening cement has been used in these blocks or anchorages, the test shall not be made until at least two days have elapsed after concreting.

Each section of pipeline shall be slowly filled with water and all air shall be expelled from the pipe by tapping at points of highest elevation before the test is made and plugs inserted after the test have been completed. Specified pressure as per relevant code based on the elevation of the lowest point of the line or section under test and corrected to the elevation of the test gauge, shall be applied by means of a pump connected to the pipe as directed by Engineer. The duration of test shall not be less than 5 minutes. Where the field test pressure is less than two-third the work test pressure, the period of test should be increased to at least 24 hours. If a drop in pressure occurs, the quantity of water added in order to re-establish the test pressure should be carefully measured. This should not exceed 0.1 litre/mm, dia per km of pipeline length per day for each 30 m head of pressure applied. The exposed joints shall be carefully examined and all such joints showing visible leaks shall be rectified until it becomes fully watertight. Any cracked or defective pipes and fittings as a consequence of this pressure test shall be removed from site and replaced by acceptable quality of pipes by Contractor and the test shall be repeated to the satisfaction of Engineer/Owner.

After the satisfactory completion of pressure test, the section of pipeline shall be subjected to leakage test at a pressure as specified in relevant code. The duration of test shall be 2 hrs. No pipe installation shall be accepted until the leakage is less than the number of Cum/hr. as determined by the formula;

qL =	ND ✓p 3.3

where,

q L = the allowable leakage in CUM./hr.

N = number of joints in the length of the pipeline D = diameter in mm. and

p = the average test pressure during the leakage test in kg./sq.cm.

Should any test of pipe laid disclose leakage greater than that specified above the defective joints shall be repaired by Contractor at no extra cost to the Engineer until the leakage is within the specified allowance

Necessary equipment and water used for testing shall be arranged by Contractor at his own cost. Damage during testing shall be Contractor's responsibility and shall be rectified by him at no extra cost to the Engineer/Owner. Water used for testing shall be drained out from the pipe to safe location and should not be released in the excavated trenches.

After the tests mentioned above are completed to the satisfaction of Engineer/Owner, the backfilling of trenches shall be done as per specification.

  - Disinfection of water mains

The mains intended for potable water supplies should be disinfected before commissioning them for use.

After pressure testing the main, it should be flushed with water with sufficient velocity to remove all dirt and other foreign materials. When this process has been completed the process of disinfection (using liquid chlorine, sodium or calcium hydrochloride) can proceed by one of the following methods.

  - Continuous feed

In this method, water from the distribution system or other approved source and the chlorine are fed at a concentration of at least 20 to 50 mg/litre. A properly adjusted hydrochloride solution injected into the main with a hydro chlorinator, or liquid chlorine injected into the main through a solution feed chlorinator and booster pump shall be used. The residual chlorine should be checked at intervals to ensure that the proper level is maintained. Chlorine application should continue until the entire main is filled. The water should remain in the main for a minimum of 24 hours, during which time all valves, hydrants, etc. along the main should be operated to ensure their proper disinfection. Following the 24 hours period not less than 10 mg/l residual chlorine should remain in the main.

  - Slug method

In this method a continuous flow of water is fed with a constant dose of chlorine but with rates proportioned to give a chlorine concentration of at least 300 mg/l. The chlorine is applied continuously for a period of time to provide a column of chlorinated water that will contact all interior surface of the main for a period of at least three hours. As the slug passes tees, crosses etc., valves must be properly operated to ensure their disinfection. This method shall be used principally for large diameter mains.

Regardless of the method used, it is necessary to make certain that back flow of the strong chlorine solution into the supplying line does not occur. The' chlorinated water should be flushed to waste until the remaining water has a chlorine residual approximating to 0.2 mg/l that throughout the rest of the system bacteriological tests should be taken and if the result fails to meet minimum standards, the disinfecting procedure must be repeated and the results again tested before placing the main in service.

- Measurement

The measurement for pipe laying shall be on running metres of net length along the centre line of pipe as laid including specials. The length of pipes shall not include the portion of spigots within the sockets of fittings and pipes.

The rate for providing and laying of D.I. pipes shall be deemed to include the extra excavation required for ordinary bedding of pipes as per IS: 783 and also for sockets or flanges if any and cost of jointing material.

  - Procedure of measurements

- Length (L): As per the actual length of pipe and fittings / specials laid at work site.

- Trench Width (B): For payment of excavation, the width of trench shall be considered as O. D. + 600 mm. only where O.D. is the outside diameter of the pipe in mm.

- Depth (D): Average depth of trench from ground level to invert of pipe and fittings.

- Notes

Fencing provided along the sides of trenches and pits shall not be paid for separately and Contractor shall take into account the costs of such works and quote accordingly.

In case of the road metal packing or dressed stones not being deposited as specified or being mixed up with excavated materials and not available for the reinstatement of road / pavement, the cost of the new metal packing or dressed stones required shall be charged to Contractor by the Employer / Engineer.

Service lines if damaged during excavation shall be made good either by Contractor or by other agency as the Employer/ Engineer may decide and wholly in either case at the expense of Contractor.

Contractor shall not be paid any additional compensation for excess excavation over what is specified as well as for any remedial measures that are specified.

The excess excavated material shall be carried away from site of works as specified, failing which in view of public safety and traffic convenience the Employer / Engineer may carry out the work by any other agency at Contractor's risk and cost.

Portion of shoring left in the excavated trenches or pits shall be measured and paid separately, if instructed by the Employer / Engineer to do so.

Sub-Section - WS - 4

Technical specifications for HDPE pipes and UPVC pipes

## Sub-Section - WS - 4

## Technical specifications for HDPE pipes and UPVC pipes

Contents

Clause no.		Description

- .	Scope

- Applicable codes

- Designation

- Colour

- Materials

- Handling, transportation storage and lowering of pipes

- Lowering, laying of pipes

- Jointing of pipes

- Bedding, Backfilling and Compaction

- Thrust block

- .	Inspection & testing

- Tests to establish portability of work

- Testing of pipes

- Marking

- Measurement

# Sub-Section - WS - 4: Technical specifications for HDPE pipes and UPVC pipes

- Scope

This specification covers the requirements for successfully designing, manufacturing, supplying, laying, jointing and testing at works and site of High-Density Polyethylene Pipes used for water supply and UPVC pipes for sewerage system.

- Applicable codes

The manufacturing, testing, supplying, laying, jointing and testing at work sites of HDPE pipes and UPVC pipes shall comply with all currently applicable statutes, regulations, standards and Codes. In particular, the following standards, unless otherwise specified herein, shall be referred. In all cases the latest revision of the Codes shall be referred to. If requirements of this Specification conflict with the requirements of the standards / Codes, this Specification shall govern.

| Code no. | Title / Specification |
| --- | --- |
| IS 4984 | High Density Polyethylene Pipes for potable Water Supply |
| IS 2530 | Methods of test for polyethylene molding materials and polyethylene compounds |
| IS 5382 | Rubber sealing rings for gas mains, water mains and sewers. |
| IS 4905 | Methods for random sampling |
| IS 7328 | High density polyethylene materials for molding and extrusion |
| IS 7634 Part-2 | Laying & Jointing of Polyethylene (PE) Pipes |
| IS 7634 Part-3 | Plastic pipes selection, handling, storage and installation for potable water supplies - Code of practice Part 3 Laying and jointing of UPVC pipes |
| IS 9845 | Method of analysis for the determination of specific and/or overall migration of constituents of plastics material and articles intended to come into contact with foodstuffs |
| IS 10141 | Positive list of constituents of polyethylene in contact with food stuffs, pharmaceuticals and drinking water. |
| IS 10146 | Polyethylene for its safe use in contact with foodstuff, Pharmaceuticals and drinking water. |
| IS 8008 Part I to X | Injection molded high density polyethylene (HDPE) fittings for potable water supplies |
| IS 10124 | Fabricated PVC-U fittings for potable water supplies |
| IS 12818 | Unplasticized polyvinyl chloride (PVC-U) screen and casing pipes for bore / tube wells |
| IS 15328 | Unplasticized non-pressure polyvinyl chloride (PVC-U) pipes for use in underground drainage and sewerage system |

The above are only indicative. Other Codes not specifically mentioned here but pertaining to the use of HDPE pipes and UPVC pipes form part of these Specifications.

- Designation

Pipes shall be designated as per IS 4984 and IS 15328 for HDPE and uPVC pipes respectively.

  - HDPE Pipes:

The pipes shall be designated according to the grade of material, followed by pressure rating and nominal diameter, for example, PE 100 PN 6 DN 200 indicates a pipe pertaining to material grade 100 having a pressure rating 0.6 MPa and outside nominal diameter 200 mm.

  - Unplasticized non-pressure polyvinyl chloride (uPVC)

The numerical designation for the size of a pipe, other than a pipe designated by thread size, which is a convenient round number approximately equal to the manufacturing dimension in millimeter, for example 100mm OD pipe.

- Colour

The colour of the pipe shall be as specified in the relevant Indian standards.

- Materials

  - HDPE pipe

The material used for the manufacturer of pipes should not constitute toxicity hazard, should not support microbial growth, should not give rise to unpleasant taste or odor, cloudiness or discoloration of water. Pipe manufacturers shall obtain a certificate to this effect from the manufacturers of raw material by any internationally reputed organization as per the satisfaction of the engineer in charge.

The pipe shall contain no recycled compounds All pipes shall be suitable for use as pressure conduits, and shall have nominal burst values of three times the Working Pressure Rating (WPR) of the pipe for the pipes 2inches and smaller and shall have nominal burst values of three and half times the Working Pressure Rating (WPR) of the pipe for the pipes 3inches and larger.

    - Raw material

Raw material used to manufacture the HDPE pipes shall be 100% virgin PE compound or Natural black PE resin confirming to IS: 4984, IS: 7328 and ISO: 4427 for this a certification has to be given by the resin manufacturer as per clause 3.2.3 of IS: 4984.

Certificate for having passed the full-scale rapid crack propagation test as per ISO

13478 has to be given. High density Polyethylene (HDPE) used for the manufacture of pipes shall conform to designation PEEWA-45-T-006 of IS 7328. HDPE conforming to designation PEEWA-45- T-0 2 of IS 7328 may also be used with the exception that melt flow rate (MFR) shall not exceed 1.10 g/10 min. In addition, the material shall also conform to clause 5.6.2 of IS 7328.

The specified base density shall be between 94.0kg/ m3 and 946.0kg/ m3 (both inclusive) when determined at 27°C according to procedure prescribed in IS 7328 The value of the density shall also not differ from the nominal value by more than 3 kg/ m3 as per 5.2.1.1 of IS 7328. The MFR of the material shall be between 0.41 and 1.10 (both inclusive) when tested at 90°C with nominal load of 5 kgf as determined by method prescribed in IS 2530. The MFR of the material shall also be within ± 20 percent of the value declared by the manufacturer.

The resin shall be compounded with carbon black. The carbon black content in the material shall be within 2.5 ±0.5% and the dispersion of carbon black shall be satisfactory when tested as per IS 2530.

    - Anti-oxidant

The percentage of anti-oxidant used shall not be more than 0.3 percent by mass of finished resin. The anti-oxidant used shall be physiologically harm less and shall be selected from the list given in IS 10141.

    - Reworked material

No addition of Reworked/ Recycled Material from the manufacturer's own rework material resulting from the manufacture of pipes is permissible and the vendor is required to use only 100% virgin resin compound.

    - Maximum ovality of pipe

The outside diameter of pipes, tolerance on the same and ovality of pipe shall be as given in table 2 of IS 4984. Ovality shall be measured as the difference between maximum outside diameter and minimum outside diameter measured at the same cross section of the pipe, at 300 mm away from the cut end. For pipes to be coiled the ovality shall be measured prior to coiling. For coiled pipes, however, re-rounding of pipes shall be carried out prior to the measurement of ovality.

    - Wall thickness

The minimum & maximum wall thickness of pipe for the PE 100 grade shall be as given in table 5 in IS: 4984.

    - Length of straight pipe

The length of straight pipe used shall be more than 6 m or as agreed by engineer in charge. Short lengths of 3 meter (minimum) up to a maximum of 10% of the total supply may be permitted.

    - Coiling

The pipes supplied in coils shall be coiled on drums of minimum diameter of 25 times the nominal diameter of the pipe ensuring that kinking of pipe is prevented. Pipe beyond 110mm dia shall be supplied in straight length not less than 6m.

    - Workmanship / Appearance

Pipes shall be free from all defect including indentations, delaminating, bubbles, pinholes, cracks, pits, blisters, foreign inclusions that due to their nature degree or extent detrimentally affect the strength and serviceability of the pipe. The pipe shall be as uniform as commercially practicable in colour opacity, density and other physical properties as per relevant IS Code or equivalent International Code. The inside surface of each pipe shall be free of scouring, cavities, bulges, dents, ridges and other defects that result in a variation of inside diameter from that obtained on adjacent unaffected portions of the surface. The pipe ends shall be cut clearly and square to the axis of the pipe.

    - Fittings & specials

All HDPE fittings/ specials shall be fabricated in accordance with IS: 8360 (Part I & III). PE Injection molded fittings shall be as per IS: 8008 (Part I to IX). All fittings/specials shall be fabricated or injection molded at factory only. No fabrication or molding will be allowed at site, unless specifically permitted by the Engineer. Fittings will be butt welded on to the pipes.

For industrial connections and smaller diameter (<90mm OD) polyethylene pipes where the working pressures do not exceed 1.0Mpa, jointing by mechanical compression fittings is recommended. The Compression Fittings shall be as per the Specification given in PE Fittings Specifications

Certification from international recognized organization should be submitted for compression fittings. Molded PE Fittings shall be homogeneous throughout, and free of visible cracks, holes, foreign inclusions, blisters, dents, or other injurious defects. The molded PE fittings shall be as uniform as commercially practicable in color, opacity, density, and other physical properties, as the pipe.

The size and length of jointing threads, where applicable shall be suited to fit the threads of Galvanized Iron (GI) Pipes manufactured as per IS 1239: 1990. A tight fit test with a BIS marked GI Pipe shall be demonstrated.

Butt Fusion Fittings - Molded & fabricated fittings shall have a pressure rating equal to the pipe unless otherwise specified in the plans. Fabricated fittings are to be manufactured using Data Loggers. Temperature, fusion pressure and a graphic representation of the fusion cycle shall be part of the quality control records. All fittings shall be suitable for use as pressure conduits and shall have nominal burst values of three and one-half times the Working Pressure Rating (WPR) of the fitting.

Electro fusion Fittings - Fittings shall have a pressure rating equal to the pipe unless otherwise specified on the plans. All electro fusion fittings shall be suitable for use as pressure conduits and shall have nominal burst values of three and one-half times the Working Pressure Rating (WPR) of the fitting.

Flanged and Mechanical Joint Adapters - Fittings shall have a pressure rating equal to the pipe unless otherwise specified on the plans.

    - Bends

HDPE bends shall be plain square ended conforming to IS: 8360 Part I & III Specifications. Bends may be fabricated by jointing several small sections of pipes to reach the required angle.

    - Tees

HDPE Tees shall be plain square ended conforming to IS: 8360 Part I & II Specifications. Tees may be equal tees or reduced take off tees. Tees may be molded or fabricated from pipes elements.

    - Reducers

HDPE Reducers shall be plain square ended conforming to IS: 8008 Part I & VII Specifications. Reducer must be molded.

    - Flanged HDPE pipe ends

HDPE Stub ends shall be square ended conforming to IS: 8008 Part I & VII Specifications. Stub ends will be welded on the pipe. Flange will be of slip on flange type as described below.

    - Slip-on flanges

Slip-on flanges shall be metallic flanges covered by epoxy coating or plastic powder coating. Slip-on-flanges shall be conforming to standard mating relevant flange of valves, pipes etc. Nominal pressure rating of flanges will be PN10.

    - Tapping saddles

Tapping saddles shall be of PP with suitable female threaded tapping or Electro fusion saddle as per site requirements.

  - Unplasticized non-pressure polyvinyl chloride (uPVC):

    - Raw material

The material from which the pipe is produced shall consist substantially of polyvinylchloride, to which may be added only those additives that are needed to facilitate the manufacture of the compound and the manufacture of sound and durable pipe of good surface finish, mechanical strength and opacity under conditions of use. None of these additives shall be used separately or together in quantities sufficient materially to impair the fabrication or welding properties of the pipe, or to impair its chemical and physical or mechanical properties (in particular long-term mechanical strength and impact strength) as defined in this standard.

The material shall contain a minimum of 0.3 percent of rutile grade titanium dioxide. When sealing rings are retained by means of retaining devices (rings or caps), the devices may be made from polymers other than PVC-U, provided they conform to the same functional dimensions and test requirements as applied to sockets with either loose or fixed sealing rings.

The manufacturer's own rework material conforming to the requirements given in the IS 15328 is permissible.

    - Reworked material

No other rework material shall be used.

    - Joints:

For the best performance of the pipeline, jointing of the pipe plays a major part. PVC sewer pipes are manufactured conforming to IS 15328 with two types of joints.

      - Solvent weld joint

      - Rubber Ring Joint.

- Solvent Cement Joint:

Special grade of cement is available for jointing the underground sewerage pipes to give a monolithic joint which are totally leak-proof and this should be used which is supplied by the manufacturer of pipes.

The inside of the socket should be cleaned thoroughly to remove any dust and foreign particles adhering to the inside surface of the socket before applying a thin coat of cement on the inside surface of the socket. The socket inside should be smooth and should not be scratched with blades and rough sand paper to remove the dirt or foreign particles sticking to the surface. The thin layer applied should cover the entire surface of the socket and applying too much of solvent cement should be avoided as it will pool on the bottom side of the socket and create a hole in the pipe socket due-to solvent nature of the cement.

The same way the spigot end of the other pipe which is to be jointed to the socket of the pipe already applied with solvent cement should be cleaned of any dirt and foreign particles sticking to it and in this case the spigot portion can be cleaned uniformly with a soft grained emery sheet if needed. After cleaning the spigot end of the pipe, mark the depth of the coupler on the spigot and apply two layers of cement on the spigot up to the marking.

Insert the spigot into the socket after aligning the pipe and push the spigot fully in to the socket till the marking comes in line with the socket end and hold it for a few minutes. If the jointing pressure is removed immediately after the spigot is inserted, the spigot may come out and the jointing will be defective. DO NOT TWIST THE SPIGOT ONCE IT IS HOME INSIDE THE SOCKET.

The excess cement that comes out of the socket at the end of the spigot should be wiped clean with a cloth and allow the joint to cure for 24 hours before testing the joint for pressure are commissioning the line.

Ensure that the cement is applied with a brush and close the lid of the solvent cement container immediately after taking out the cement for jointing. Store the cement in cool and dark place. While using the cement at the field do not keep it under direct sunlight as it will polymerize the solvent and the cement will lose its dissolving character.

The following table will give the number of joints that can be made with one litre of special grade cement.

| Size of Pipe OD, mm | Number of Joints per litre of Cement |
| --- | --- |
| 110 | 50 |
| 125 | 45 |
| 160 | 25 |
| 200 | 5 |
| 250 | 9 |
| 315 | 5 |
| 400 | 4 |
| 500 | 3 |

The above table is an indicative with the usage of cement in the proper manner. It may vary due to temperature conditions at site and hence this estimate should not in no way used to restrict the proper application of solvent cement for obtaining best monolithic joint.

DO NOT USE FIRE NEAR THE SOLVENT CEMENT AS IT IS HIGHLY INFLAMMABLE. DO NOT SMOKE WHILE DOING THE JOINTING WHICH IS VERY DANGEROUS.

- Elastomeric sealing rings

The Sewerage pipes conforming to IS 15328 also are manufactured with integral Rubber Ring Joint on one end of the pipe and the spigot end is with a chamfer to gain entry into the rubber ring socket. Apply soft soap on the rubber ring and also on the spigot of the pipe up to a length that is marked for the socket depth insertion. Then align the spigot into the socket till the chamfered end touches and compress the rubber ring in the socket. In case of smaller diameter pipe, a slight push of the pipe into the socket will drive the spigot in to the socket compressing the rubber ring around the OD of the pipe. In case of larger diameter pipes, it is essential that we tap the pipe with hammer from the other end of the pipe which will have the socket end. However, the tapping with hammer should not be done directly on the socket. Instead, place a 1/2 an inch thick wooden plank, the width of the plank being slightly more than the socket diameter and tap the wooden plank with hammer to drive the spigot in to the socket of the other pipe. Care should be taken to maintain the alignment of the spigot pipe which is being tapped into the socket to prevent dislocation of rubber ring from the socket groove. DO NOT USE SOLVENT CEMENT WITH THE RUBBER RING JOINTS.

These rings shall be free from substances (for example, plasticizen) that can have a detrimental effect on the polyvinyl chloride of the pipes or fittings used in conjunction with the pipes. The design of the profile and dimensions of the sealing ring is left to the manufacturer, as long as the pipe with the sealing ring meets the requirements of this standard. Where the design of the socket is such that the sealing ring is not firmly fixed in position, the housing for the ring shall be so designed as to minimize the possibility of the ring being dislodged during insertion of the pipe (or spigot of a fitting) to complete the joint.

Elastomeric sealing rings shall be in accordance with one of the 6 types (Type 1 to Type 6) of IS S382. The manufacturer has to, however, specify the type of sealing ring (namely Type 1, 2, 3, 4, 5 or 6) that is being offered.

    - Performance requirements:

      - Internal Hydrostatic Pressure:

When tested in accordance with IS 15328-2003 the joint, when assembled according to the manufacturer's instructions and subjected to an angular deflection, a, minimum of 2°aswell as a diametric deflection (distortion) of 5 percent of the outer diameter, shall withstand an internal pressure of up to and including 0.05 MPa (0.5 bar) for a minimum of 15 minute without leakage.

      - Internal Negative Hydrostatic Pressure (Internal Vacuum)

When tested according to the method described in IS 15328-2003, the joint, when assembled according to the manufacturer's instructions and subjected to an angular deflection, a minimum of 2° as well as a diametric deflection (distortion) of 5 percent of the outer diameter, shall withstand an internal negative pressure (internal vacuum) of up to and including 0.03 MPa (0.3 bar) for a minimum of 15 min without leakage.

- Handling, transportation storage and lowering of pipes

During handling, transportation, storage and lowering, all sections shall be handled by such means and in such a manner that no distortion or damage is done to the section or to the pipes as a whole.

The following procedures should be followed so as to eliminate potential damage to pipes and fittings and to maintain maximum safety during unloading, lifting and lowering.

- Pipes must not be stored or transported where they are exposed to heat sources likely to exceed 60oC.

- Pipes shall be stored such that they are not in contact with direct sunlight, lubricating or hydraulic oils, petrol, solvents and other aggressive materials.

- Scores or scratches to a depth of greater than 10% or more of wall thickness are not permissible; any pipes having such defects should be strictly rejected.

- PE pipes should not be subjected to rough handling during loading and unloading operations. Rollers shall be used to move, drag the pipes across any surface.

- Only polyester webbing slings should be used to lift heavy PE (>315mm) pipes by crane. Under no circumstances, chains, wire ropes and hooks be used on PE pipes.

- Pipes shall not be dropped to avoid impact or bump. If any time during handling or during installation, any damage, such as gouge, crack or fracture occurs, the pipe shall be repaired if so permitted by the competent authority before installation.

- During coiling care should be taken to maintain the coil diameter at or above the specified minimum to prevent kinks. Coiling shall be done when the pipe attains the ambient temperature from the extruder. In uncoiling or recoiling care should be taken that sharp objects do not scour the pipe.

- When releasing coils, it must be remembered that the coil is under tension and must be released in a controlled manner. The end of the coil should be retained at all times, then the straps released steadily, one at a time. If the coil has bands at different layers of the coil, then they should be released sequentially starting from the outer layers. The amount of the energy locked up in the coil will depend on the size of the pipe, the SDR of the pipe, and the size of the coil.

- Straight lengths should be stored on horizontal racks giving continuous support to prevent the pipe taking on a permanent set.

- Bare coils shall be wrapped with hesian cloth for long distance (> 300Kms) transportation. The truck used for transportation of the PE pipes shall be exclusively used of PE pipes only with no other material loaded - especially no metallic, glass and wooden items. The truck shall not have sharp edges that can damage the Pipe.

- Pipes manufactured at factory are to be carried to the site of work directly or stacked suitably and neatly along the alignment/road side/elsewhere near by the work site or as directed by the Engineer.

- Damages during transit, handling, storage will be to the Contractor's account and replacement for such pipes has to be made by the Contractor without any extra cost as directed by the Engineer.

- Handle pipe and fittings to insure delivery in a sound undamaged condition.

      - Lowering, laying of pipes

Each pipe shall be thoroughly checked for any damages before laying and only the pipes which are approved by the Engineer shall be laid.

While installing the pipes in trenches, the bed of the trench should be level and free from sharp edged stones. In most cases, the bedding is not required, as long as the sharp and protruding stones are removed, by sieving the dug earth, before using the same a backfill material. While laying in rocky areas suitable bed of sand or gravel should be provided. The fill to about 10 to 15 cm above the pipe should be fine sand or screened excavated material. Where hard rock is met with, bed concrete M 15, 15 cm or 20cm thick sand bed as approved by the engineer may be provided.

As PE pipes are flexible, long lengths of fusion-jointed pipes having joints made above ground can be rolled or snaked into narrow trenches. Such trenches can be excavated by narrow buckets.

During the pipe laying of continuous fusion jointed systems, due care and allowance should be made for the movements likely to occur due to the thermal expansion/contraction of the material. This effect is most pronounced at end connections to fixed positions (such as valves etc) and at branch connections. Care should be taken in fixing by finishing the connections at a time the length of the pipe is minimal (lower temperature times of the day).

For summer time installations with two fixed connection points, a slightly longer length of PE pipe may be required to compensate for contraction of the pipe in the cooler trench bottom.

The final tie-in connections should be deferred until the thermal stability of the pipeline is achieved.

The flexibility of polyethylene pipes allows the pipe to be cold bend. The fusion jointed PE pipe is also flexible as the plain Pipe. Thus the total system enables directional changes within the trench without recourse to the provision of special bends or anchor blocks. However, the pipe should not be cold bend to a radius less than 25 times the OD of the pipe.

The Installation of flanged fittings such as connections to sluice/air/gate valves and hydrant tees etc., requires the use of stub ends (collars/flange adaptors complete with backing rings and gaskets. Care should be taken when tightening these flanges to provide even and balance torque.

Provision should be made at all heavy fittings installation points for supports (such as anchoring of the flange in the soil) for the flange joint to avoid the transfer of valve wheel turning torque on to the PE flange joint.

PE pipe is lighter than water. Hence care should be taken for normal installations where there could be a possibility of flooding of the trench thus the trench shall be kept free of water till the jointing has been properly done.

When flooded, some soils may lose cohesiveness, which may allow the PE pipe to float out of the ground. Several design checks are necessary to see if groundwater flotation may be a concern. Obviously, if the pipeline typically runs full or nearly full of liquid, or if groundwater is always below the pipe, flotation may not be a significant concern.

However, weights by way of concrete blocks (anchors) are to be provided so that the PE pipe does not float when suddenly the trench is flooded and the soil surrounding the pipe is washed away. Thus site conditions study is necessary to ensure the avoidance of flotation.

Pipe embedment backfill shall be stone-free excavated material placed and compacted to the 95% maximum dry density.

      - Jointing of pipes

The pipe shall have a jointing system that shall provide for fluid tightness for the intended service conditions. Appropriate jointing for HDPE pipe as per IS 4984 shall be selected considering site and working condition, pressure and flow of liquids.

Sections of polyethylene pipe should be joined into continuous lengths on the jobsite above ground. The joining method shall be the butt fusion method and shall be performed in strict accordance with the pipe manufacturer's recommendations. The butt fusion equipment used in the joining procedures should be capable of meeting all conditions as per ISO 12176. The butt fusion joining will produce joint weld strength equal to or greater than the tensile strength of the pipe itself. All welds will be made using a Data Logger to record temperature, fusion pressure, with a graphic representation of the fusion cycle shall be part of the Quality Control records.

Mechanical joining will be used where the butt fusion method can not be used. Mechanical joining will be accomplished by either using a HDPE flange adapter with a Ductile Iron back-up ring or HDPE Mechanical Joint adapter with a Ductile Iron back- up ring.

Socket fusion, hot gas fusion, threading, solvents, and epoxies will not be used to join HDPE pipe.

Only trained and technically qualified for the welding methods are to be employed for the welding operation. Welding to be carried out only through the manufacturer authorized person. Manufacturer should submit valid and authentic certificate for each person those who are performing welding at site before starting of the work to the client.

      - Welding procedure

Jointing between HDPE pipes and specials shall be done as per the latest IS: 7634 part II. Method of jointing between the pipes to pipes and pipes to specials shall be with butt fusion welding using automatic or semi-automatic, hydraulically operated, superior quality butt fusion machines which will ensure good quality butt fusion welding of HDPE pipes. If approved by the concerned Engineer, jointing with PP compression fittings may be carried out for smaller diameters of PE pipes (up to 110mm).

      - Bedding, backfilling and compaction

  - Bedding

In case of sandy strata, no separate bedding is required. However, the bottom face / trench bed where pipe shall be placed shall be compacted to provide a minimum compaction corresponding to 95% of maximum dry density. The pipe bedding should be placed so as to give complete contact between the bottom of the trench and the pipe.

  - Back filling

Backfilling should be placed in layers not exceeding 15cm thickness per layer, and should be compacted to a minimum of 95% maximum dry density. The refilling should be done on both sides of pipe together & height difference in earth fill on each side should not be more to cause lateral movement of pipe.

Most coarse-grained soil are acceptable. This may comprise of gravel or sand. However silty sand, clayey sand, silty and clayey gravel shall not be used unless proposed to be used in conjunction with gravel or clean sand.

It is very important that the pipe zone backfill material does not wash away or migrate into the native soil. Likewise, potential migration of the native soil into the pipe zone backfill must also be prevented.

Heavy earth moving equipment used for backfilling should not be brought until the minimum cover over the pipe is 90 cm in the case of wide tracked bulldozers or 120 cm in the case of wheeled roaders or roller compactors.

  - Compaction

Vibratory methods should be used for compaction. Compaction within distances of 15 cm to 45 cm from the pipe should be usually done with hand tempers. The backfill material should be compacted not less than 95% of maximum dry density.

      - Thrust block

RCC thrust block should be suitably designed & provided at bends and at places of reduction in cross section to take care of trust.

      - Inspection & testing

Pipes, fittings & specials shall be inspected for defects before installation and fusion by the client. Defective, damaged or unsound pipe will be rejected.

      - Tests to establish portability of work

Pipe specimen shall be subjected to tests specified below in order to establish the suitability of these pipes for use in carrying potable water:

- Smell of the extract

- Clarity of the colour of the extract

- Acidity and alkalinity

- Global migration UV absorbing material Heavy metals

- Un-reacted monomers (styrene) and Biological tests

      - Testing of pipes

Pipes shall be given different Performance Tests as per IS: 4984 (clause 8) and Notch Test as per ISO: 4427 for ensuring quality of pipes.

  - Hydraulic test

    - Pipes shall be given hydraulic tests for ensuring quality of manufacture as per specification.

    - The pressure-testing medium shall be clean water only. The HDPE pipe shall be filled with water, raised to test pressure and allowed to stabilize Any trapped air is to be bleeded off by suitable air release mechanism at the end of the pipe section. While the test section is being filled, venting at high points may be necessary topurge air pockets. Failure to do this will give false notion of pipe having been filled and while testing the pipe the air pockets may get compressed and hazards may occur.

    - Field Leak Testing of Polyethylene Pressure Piping Systems shall be in accordance with Hydrostatic Pressure. For pressure piping system the maximum allowable test pressure is 1½ times the system design operating pressure or Pipe rating whichever is higher at the lowest point in the system.

    - For any test pressure, the total test pressure time including initial pressurization, initial expansion, and time at test pressure must not exceed three (3) hours, ideal being one to 1½ hour. If the test is not complete due to leakage, equipment failure etc; the system shall be depressurized the same shall be allowed to 'relax' for at least eight hours, before bringing the section to test pressure again.

    - The pipe tested shall be signed with glass marking pencil (white) by the company engineer and customer site engineer, before the pipe is buried. Location, length and the date of testing shall be duly signed by company and site engineers are to be kept as a record.

  - Hydraulic characteristics of pipes

When subjected to internal creep rupture test in accordance with procedure given in BIS standards and or ISO  67, the pipes under test shall show no signs of localized swelling, leakage or weeping and shall not burst during the prescribed test period. The temperatures, duration of test and induced stress for the test shall conform to those specified in Table below:

| Hydraulic characteristic requirements of pipes |  |  |  |
| --- | --- | --- | --- |
| Sl. No. | Test temp 0C | Test duration (h) | Induced stress in MPA |
| 1 | 80  | 1000 | 5 |
| 2 | 80  | 165 | 5.5 |

  - Reversion test

The pipe shall be tested according to the procedure specified in IS 4984. The value of the longitudinal reversion shall not be greater than 3 percent.

  - Overall migration test

When tested from a composite sample of minimum 3 pipes as per IS 9845 the overall migration of constituents shall be within the limits stipulated in IS 10146.

  - Resistance to slow crack growth

The pipes shall be tested for their slow crack growth resistance in-house or at an independent organization as per ISO 13479 shall have the following test results when tested as per annexure A of IS 4984: 1995. The manufacturer shall submit such a certification for the material (tested on any pipe > 110mm) as a part of their Vendor Accreditation evaluations. Where necessary the user may insist on the test in their presence.

| Slow crack growth - ISO 13479 |  |  |  |
| --- | --- | --- | --- |
| Sl. No. | Test temp 0C | Test duration | Pressure |
|  | 80  | > 165 | 9.2 |

  - Fusion qualification

The manufacturer of pipe and fittings supplied under this specification shall establish and qualify heat fusion procedures for the joining of the materials supplied, with a documented proof of availability of welding equipment as per ISO 12176. Qualified fusion procedures, with appropriate supporting data, shall be furnished to the purchaser along with tender.

  - Marking

Each straight length of pipe shall be clearly marked in indelible ink / paint on either end and for coil at both ends or hot embossed on white base with every meter throughout the length of pipe / coil with the following information

- Manufacturers name / trade mark

- Designation of pipe (as per clause 3.1)

- Lot number / batch number

  - Measurement

The net length of pipes as laid or fixed shall be measured in running meters correct to a cm. Specials shall be excluded and measured and paid separately under the relevant item. The portion of the pipe at the joints (inside the joints) shall not be included in the length of pipe work. Excavation, refilling, masonry and concrete work wherever required shall be measured and paid for separately under relevant items of work.

## Sub-Section - WS - 5 Technical specifications for valves

# Sub-Section - WS - 5 Technical specifications for valves

Contents

Clause no.			Description					Page nos.

- Scope

- Codes and standards

- General

- Butterfly valve

- Sluice valves

- Non-return valve

- Air valve

- Electric actuator

- Cleaning

- Inspection and tests

- Painting and corrosion protection

- Drawings

- Name plates

- Information to be furnished after the award of contract

# Sub-Section - WS - 5: Technical specifications for valves

      - Scope

This specification covers the design requirements, features of construction, inspection and testing of all valves.

      - Codes and standards

The design, material, construction, manufacture, inspection, testing and performance of valves shall comply with all currently applicable statutes, regulations and safety codes in the locality where the equipment will be installed. The equipment shall also conform to the latest editions of applicable codes and standards. Nothing in this specification shall be construed to relieve the VENDOR of this responsibility.

      - General

Valves shall be as per internationally recognised standards. Flanges shall be machined on faces and edges and conform to ISO 7005, IS 6392 or BS 4504.

Valves shall be double flanged type and the face shall be parallel to each other and flange face should be at right angles to the valve centerline. Back side of valve flanges shall be machined or spot faced for proper seating of the head and nut.

Valve buried or installed in underground chamber, where access to a hand wheel would be impractical shall be operated by means of extension spindle and / or keys.

Valve of diameter 450 mm and above shall be provided with lifting eyes and shall have detachable bolted covers for inspection, cleaning and servicing.

Valve shall be suitable for frequent operation as well as operation after long periods of idleness in either open or closed position.

The valve stem, thrust washers, screws, nuts and all other components exposed to the water shall be of a corrosion resistant grade of stainless steel.

Valves shall be free from sharp projections.

All valves shall be so designed that the hand wheel moves in a clockwise direction to close the valve. The face of the hand wheel shall be clearly marked with the words 'open' and close and an arrow to indicate the direction for opening. All hand wheels shall be fitted with the name plate.

The design of valves shall ensure a streamlined passage and low pressure drop. The seats and discs shall be easily renewable. Valve discs shall be of such design as to keep the seats tight when the valve body is subjected to pressure, temperature variations and pipeline stresses.

Valves that are to be kept locked in full 'open' / 'close' position shall be provided with a non-detachable locking arrangement.

Gland packings should be of material free from asbestos.

Motor operators shall be designed to close the valves within the time specified from the full open position.

Flow directions shall be clearly embossed on the valve body for valves whose function and service ability is affected by fluid flow direction.

      - Butterfly valve

Butterfly valve shall be as per IS 13095 / BS 5155. Valve shall suitable for mounting in any position.

Valves shall be double flanged short body type and Cone-sphere eccentric design.

The valve seat shall be secured to the valve body. When the valve is fully closed, a seal shall seat firmly so as to prevent leakage. The seat surfaces shall be machined smooth to provide a long life for the seal.

Valves should have two stub shafts, extending at least 2 times their dia, within a robust housing on either side fitted with PTFE lined stainless steel.

The valve seat on the body should be integral with it to preclude any leakage from beneath the ring/'O' ring when the disc is closed.

The valve seal shall be replaceable and securely clamped to the edge of the disc by stainless steel seal retention members, or equivalent so as to prevent leakage and to hold the seal securely during operation. The seal retention member shall be securely clamped with stainless steel fasteners. All fasteners shall be set flush so as to offer the least resistance possible to the flow through the valve.

Seal ring arrangement should be made to prevent the seal ring becoming loose in service.

Valve disc, shaft and cotter pins, actual working stress at designed pressure should not exceed 40% of the yield stress of material.

Valve shall be suitable for throttling purpose.

All valve spindles and hand wheels shall be positioned to give good access for operational personnel.

Valves should be drop tight and designed for flow in either direction.

Valve of diameter 450 mm and above shall be provided with enclosed gear arrangement for ease of operation. The operation gear shall be such that they can be opened and closed by one man against an unbalanced head 25% in excess of the maximum specified rating. Valve and any gearing shall be such as to permit manual operation in a reasonable time and not exceed a required rim pull of 400 N.

All hand wheels shall be arranged to turn in a clockwise direction to close the valve, the direction of rotation for opening and closing being indicated on the hand wheels.

In addition to providing end of travel stops in the gear box, an integral stopper in the body to be provided to prevent over travel of disc during closure.

Gear box must be self-locking type, with a continuous indicator. Travelling nut and screw type of gear boxes are not acceptable.

All valve operators shall be equipped with adjustable mechanical stop-limiting devices to prevent over-travel of the valve disc in the open and closed positions. Either end of the worm shaft must be provided with needle roller bearing to take on the lateral thrust. The design must ensure thrust is arrested within the worm housing.

The housing for the gearing must be enclosed and sealed in such a way that there is no leakage of oil / grease even after long period of in use and there is no ingress of rainwater. Operator for valves which are likely to be submerged in water for long period during the rainy season, must be water tight.

The hand wheels may be provided with extension and plastic cover for easy grip. Alternatively, the hand wheels must have a provision for locking with a chain and pad lock. All operators when fitted to the valve shaft must ensure clock wise closing and this must be indicated on the housing. A mechanical indicator is to be provided to show disc travel and end of travel.

Data sheet for butterfly valves

| Sl. No | Description |  | Particulars |
| --- | --- | --- | --- |
| . | Size | : | 300 & 600 NB |
| 2. | Rating (Kg/sq.cm) | : | As specified in the scope of work |
| 3. | Drilling | : | IS 1538 Table 4 & 6 |
| 4. | Material of construction | : |  |
|  | Body | : | CI IS 210 Gr. FG 260 |
|  | Disc |  | SG IS 1865 Gr. 500 / 7 |
|  | Shaft, Cotter | : | Stainless steel AISI 431 |
|  | Bearing | : | PTFE lined stainless steel, self-lubricated |
|  | Seat | : | Monel 60 integral |
|  | Seal Ring | : | Nitrile / EPDM |
|  | Seal Retaining Ring | : | S.G.Iron |
|  | Internal fasteners | : | Stainless steel AISI 304 |
| 5. | Gear Box |  |  |
|  | Housing and Cover |  | CI Gr 25/SG Gr 500-7/CS Gr WCB |
|  | Quadrant |  | SG Gr 500-7 |
|  | Spur Gears |  | EN-8 with hardened (by nitriding) |
|  | pinions |  | EN- 9 |
|  | Worm |  | EN- 9, hardened (by nitriding) |
|  | Bearings |  | FAG/SKF/Equivalent |
|  | "O" rings |  | Nitrile rubber |
|  | Hand wheel |  | Steel / SG Iron |
|  | Make |  | Bidder to confirm |
| 6. | Shop Testing |  |  |
|  | Seat leakage (Minimum for 5 minutes) | : | 1 time of maximum working pressure |
|  | Body (Minimum for 5 minutes) | : | 1.5 times of maximum working pressure |
|  | Material Test Certificate | : | Required for all material |

      - Sluice valves

Sluice valve shall conform to IS 780 and IS 2906 / IS 14846 or relevant internationally recognised standards.

They shall be of rising or non-rising spindle type depending on application. The valve shall be furnished with a bushing arrangement for replacement of packing without leakage. They shall also have renewable channel and shoe linings. The gap between the shoe and channel shall be limited to 1.5 mm.

The gate face rings shall be screwed into the gate or alternatively securely pegged over the full circumference.

Valves of 450 mm and above shall be provided with thrust bearing arrangement for ease of operation.

Valves of diameter 450 mm and above shall be provided with enclosed gear arrangement for ease of operation. The operation gear of all valves shall be such that they can be opened and closed by one man against an unbalanced head 15% in excess of the maximum specified rating. Valve and any gearing shall be such as to permit manual operation in a reasonable time and not exceed a required rim pull of 400 N.

Valves 450 mm and above shall be provided with a drain and air plug.

All valves, spindles and hand wheels shall be positioned to give good access for operational personnel.

All hand wheels shall be arranged to turn in a clockwise direction to close the valve, the direction to close the valve, the direction of rotation for opening and closing being indicated on the hand wheels.

Valves 300 mm dia & above shall be provided with an antifriction device / ball thrust bearing arrangement to minimize friction between spindle collars and casting. These should be housed away from wet chamber and should have facility for periodic greasing.

Valves 300 mm and above shall be fitted with gunmetal channel and shoe arrangement, the clearance being controlled between 2 to 3 mm throughout the door travel. The channels should be fixed from inside. Puncturing the body for fixing of channels is not permitted.

All valve doors when fully closed, would ensure door faces are riding on body seat ring by at least 50% of the width of seat ring and there is sufficient room for wear travel.

All face and seat rings will be force/press fitted and additionally riveted (300 NB & above) to the recess in the CI casting.

Manufacturer to justify with calculation that the valve proposed is operable within the effort parameters specified and no. of turns to ensure the time required to operate the valve from full open to full close is within reasonable limits.

The rated torque capability of each operator shall be sufficient to seat, unseat and rigidly hold in only intermediate position the sluice valve door it controls under the operating conditions specified. Operator base is to be drilled as per ISO 5210 keeping in mind the rated torque of selected operator.

The operator could be of worm/ spur type to ensure that the effort on hand wheel (did not exceeding 750 mm) is limited to 80N pull and push, unless stated otherwise in the valve specification. Either end of the worm shaft, if used, must be provided with needle roller bearings to take on the lateral thrust.

The housing for the gearing must be enclosed and sealed in such a way that there is no leakage of oil/grease even after long period of in use and there is no ingress of rain water. Operator for valves which are likely to be submerged in water for long period during the rainy season must be water tight

The hand wheels may be provided with extension and a plastic cover for easy grip. Alternatively, they may be powder coated with a mat finish. The hand wheels must have a provision for locking with chain and pad lock. All operators when fitted to the valve shaft must ensure clockwise closing and this must be indicated on the housing/ hand wheel.

A mechanical indicator is to be provided to show door travel and end of travel. Valve manufacturer to ensure that a protective thrust plate is provided between the valve and the gear operator so that no lateral thrust comes on the gear box.

Data sheet for sluice valves

| Sl. No | Description |  | Particulars |  |
| --- | --- | --- | --- | --- |
| . | Size | : | 25 mm to 300 mm NB |  |
| 2. | Rating (Kg/sq.cm) | : | As specified in the scope of work |  |
| 3. | Drilling | : | IS 1538 Table 4 & 6 |  |
| 4. | Material of construction | : |  |  |
|  | Body | : | CI IS 210 Gr. FG | Cast Steel IS 1030 |
|  |  |  | 200 / CI IS 210 Gr. | Gr. 230 - 450 W / |
|  |  |  | FG 260 | ASTM A 216 Gr. |
|  |  |  |  | WCB |
|  | Wedge | : | CI IS 210 Gr. FG | Cast Steel IS 1030 |
|  |  |  | 200 / CI IS 210 Gr. | Gr. 230 - 450 W / |
|  |  |  | FG 260 | ASTM A 216 Gr. |
|  |  |  |  | WCB |
|  | Spindle | : | Stainless steel AISI 410 / 431 |  |
|  | Seat & face rings | : | Bronze IS 318 LTB II |  |
|  | Channel & shoe | : | Bronze IS 318 LTB II |  |
|  | Drain & air plug | : | Bronze IS 318 LTB II |  |
|  | Ball thrust bearing | : | SKF or equivalent |  |
|  | Bushing arrangement | : | Halprene on bronze |  |
|  | Rivets | : | Soft annealed brass |  |
|  | Gland packing | : | Teflon coated / graphite asbestos / hemp |  |
|  | Fasteners | : | Carbon Steel |  |
| 5. | Gear Box |  |  |  |
|  | Housing and Cover |  | CI Gr 25/SG Gr 500-7/CS Gr WCB |  |
|  | Spur Gears |  | EN-8 with hardened (by nitriding) |  |
|  | pinions |  | EN-19 |  |
|  | Worm |  | EN-19, hardened (by nitriding) |  |
|  | Bearings |  | FAG/SKF/Equivalent |  |
|  | "O" rings |  | Nitrile rubber |  |
|  | Hand wheel |  | Steel / SG Iron |  |
|  | Make |  | Bidder to confirm |  |
| 6. | Shop Testing |  |  |  |
|  | Seat leakage (Minimum for 5 minutes) | : | 1time of maximum working pressure |  |
|  | Back Seat leakage (Minimum for 2 minutes) |  | 0.5 times of maximum working pressure |  |
|  | Body (Minimum for 5 minutes) | : | 1.5 times of maximum working pressure |  |
|  | Material Test Certificate | : | Required for all material |  |

      - Non-return valve

The valves shall generally conform to IS 5312 Part I & II (Single Door Type and Multi door type)

The valve shall be suitable for mounting on a horizontal pipeline and flow direction shall be clearly embossed on the valve body.

The valves shall possess high speed closing characteristics and be designed for minimum slam condition when closing.

Valves shall have in built quick closing non-slam characteristics achieved by suitable disposition of weight on door and the hydraulic passage.

Spring loaded/ spring return action or external dampening arrangement is not acceptable. If the manufacturer prefers to provide, the same to be informed to us before quoting.

In case of multi-door swing type check valve, the non-slam characteristic shall be achieved by providing suitable combination of door and hydraulic passages without any external damping arrangements or passages. The angle of sealing and door weight shall be designed to provide the most efficient working with least restriction to flow.

Valves of multi door type shall be additionally provided with a supporting foot.

All faces and seat rings shall be force/press fitted and additionally riveted (300 NB & above) to the recess in the CI casting.

Valve of diameter greater than 450 mm. shall be provided, in addition to others, feet and jacking screws. Hinge pins / shaft shall preferably be square in section to ensure positive location of flaps and provide for secure fixing.

Data sheet for non-return valves

| Sl. No | Description |  | Particulars |  |
| --- | --- | --- | --- | --- |
| . | Size | : | 300 NB |  |
| 2. | Rating (Kg/sq.cm) | : | As specified in the scope of work |  |
| 3. | Drilling | : | IS 1538 Table 4 & 6 |  |
| 4. | Material of construction | : |  |  |
|  |  |  | Cast iron valve | Cast steel valve |
|  | Body | : | CI IS 210 Gr. FG 200 / CI IS 210 Gr. FG 260 | Cast Steel IS 1030 Gr. 230 - 450 W / ASTM A 216 Gr. WCB / Cast Steel IS 1030 Gr. 230 - 450 W / ASTM A 216 Gr. WCB |
|  | Hinge pin / Stub pin | : | Stainless Steel AISI 304 (IS 6603 Gr 04 Cr 9 Ni 9) | Stainless Steel AISI 410 / 431 |
|  | Seat & Face rings | : | IS 318 Gr. LTB II |  |
|  | Rivets | : | Soft annealed brass |  |
|  | Fasteners | : | Carbon Steel |  |
| 5. | Shop testing |  |  |  |
|  | Seat leakage (Minimum for 5 minutes) | : | 1 time of maximum working pressure |  |
|  | Body (Minimum for 5 minutes) | : | 1.5 times of maximum working pressure |  |
|  | Material Test Certificate | : | Required for all material |  |

      - Air valve

Automatic air valves generally conforming to IS 14845 are to be used for evacuation of accumulated air in water mains under pressure, for the exhaust of air when such mains are being charged with water and for ventilating the mains when they are being emptied of water

The valve shall be capable of exhausting air form pipe work automatically when being filled. The air being released at a sufficiently high rate to prevent the restriction of the inflow rate. Similarly the valve shall be capable of ventilating pipe work automatically when being emptied, the air inflow rate being sufficiently high to prevent the development of a vacuum in the pipelines. The valve shall also automatically release air accumulating in pipe work during normal working conditions.

Air valve shall have two orifices in a valve for air discharge or intake together with an isolating valve to isolate the air valve proper from the main to facilitate maintenance, repair or replacement work. One of the two orifices to be used for bulk evacuation or intake, the large one, sealed by a hard vulcanite covered timber cored float (or ball). The other for evacuation of accumulated air in the pipeline under normal working condition.

For ease of operation the isolating valve is to be complete with a pair of mitre wheels, i.e., a set of bevels having a pitch cone angle of 45°.

Air valve shall be designed to prevent premature closure prior to all air having been discharged from the line. The orifice shall be positively sealed in the closed position but the float (ball) shall only be raised by the liquid and not by a mixture of air and liquid spray. The seating shall be designed to prevent the floats sticking after long periods in the closed position.

Valves must have proven kinetic design features to eliminate premature blowing shut of large orifice by the vulcanite covered timber ball due to the high velocity of emergent stream of air even at critical level of 344 mtr/sec.

The design shall be such that the higher the rate of flow (and therefore the greater the differential pressure) the greater the resultant down thrust keeping the ball glued to its seat until the last drop of air is expelled from the pipe system.

The specific gravity of the rubber / vulcanite covered timber cored ball floats in the high- and low-pressure chambers must be within 0.6 to 0.8 to ensure stipulated free board with the ball freely floating.

The isolating sluice valve should be of standard class I design except the modification in its operating arrangement. The valve shall have a pair of mitre wheel gearing for ease of operation. These are to be machine cut.

Function and performance test of air valves

When tested as below, the air passage and the function of ball floats in a valve shall be satisfactory, and the valve shall work smoothly.

The valve shall be fitted on a test bench. The pressure of the water in pipe shall be developed to working pressure, and the main valve shall be gradually opened to check the air release and float function. Compressed air shall then be slowly put into the valve through underside of the valve, and check the function of floats.

Hydrostatic test of valve body, when tested as mentioned below there shall be no leakage through pressure sustaining components and joints. There shall be no permanent deformation of any part.

The valve body (without cover and ball floats) shall be covered by a blank flange, keeping isolating valve open. Hydrostatic pressure of 1.5 times the pressure class of the valve shall be applied for duration of 5 minutes to check the water tightness of the body.

Valve seat and cock, when tested as mentioned below, shall not show any leakage.

  - High pressure orifice seat test

Orifice Seat is to be tested for one time of the working pressure to check leakage of orifice seat for duration of three minutes.

  - Low pressure orifice seat test

Subsequent to high pressure orifice performance test, hydraulic pressure shall be reduced up to half of the working pressure to check leakage of orifice seat for duration of three minutes.

Data sheet for air valves

| Sl. No | Description |  | Particulars |
| --- | --- | --- | --- |
| . | Size | : | 50 mm NB |
| 2. | Rating (Kg/sq.cm) | : | As specified in the scope of work |
| 3. | Material of construction | : |  |
|  | Body | : | CI IS 210 Gr. FG 200 |
|  | High Pressure Cover | : | CI IS 210 GR FG 200 |
|  | Low Pressure Cover | : | CI IS 210 GR FG 200 |
|  | Cowl | : | CI IS 210 GR FG 200 |
|  | High Pressure Orifice Plug | : | IS 318 Gr. LTB 2 / St. St. AISI 410 |
|  | Low pressure Seat Ring | : | Nitrile rubber (Dexine) |
|  | Isolating sluice valve | : | Conforms to IS 14846 |
|  | Spindle for sluice valve | : | Stainless steel AISI 410 |
|  | Fasteners | : | Carbon Steel |
|  | Minimum float size - Low / High pressure ball |  | 200 / 150 mm |
| 4. | Shop Testing |  | As specified in clause 7 |
|  | Material Test Certificate | : | Required for all material |

      - Electric actuator

All local controls shall be protected by a lockable cover.

Each actuator shall be adequately sized to suit the application and be continuously rated to suit the modulating control required. The gearbox shall be oil or grease filled, and capable of installation in any position. All operating spindles, gears and headstocks shall be provided with adequate points for lubrication.

The actuator shall be capable of producing not less than 1½ times the required valve torque and shall be suitable for at least 15 minutes continuous operation.

The actuator shall be suitable for continuous remote indication of door travel besides having a local mechanical indicator.

The actuator starters shall be integrally housed with the actuator in robustly constructed and totally enclosed weatherproof housing. The motor starter shall be capable of starting the motor under the most severe conditions.

The starter housing shall be fitted with contacts and terminals for power supply, remote control and remote positional indication, and shall also be fitted with internal heaters so as to provide protection against damage due to condensation. Heaters shall be suitable for single phase operation. The heaters shall be switched "ON" when the starters are "OFF" and shall be switched "OFF" when the starters are "ON".

Each valve will be tested with corresponding electric actuator and must be supplied by the valve manufacturer only.

  - Each starter shall be equipped as follows

  - 2 Nos. Three phase magnetically operated line contactors with no-volt release and electrical and mechanical interlock.

  - 1 No. Three phase terminal cut-out device.

  - 1 No. Control circuit transformer fully protected by fuses on primary and secondary circuit.

  - 1 No. Set of "Open", "Close" and "Stop" buttons.

  - 1 No. Local - Off-remote switch with padlocking facilities.

  - 1 No. Set of torque and limit switches for "Open" and "Close" positions.

  - Valve position indicator and hand wheel for manual operation.

  - Reduction gear unit.

  - Testing of actuator

Following test to be carried out at factory

Crack open	:	Against full differential / working pressure to

demonstrate efficacy of system

Smooth travel	:	From full open to full close under no flow (dry)

condition and to check soundness of limit switches

Gearbox shall have a life of 100,000 hours, and be selected in accordance with AGMA recommendation.

      - Cleaning

Prior to factory inspection, all manufacturing waste, such as metal chips and fillings, rags, debris and all other foreign matter shall be removed from the interior of each valve. All scale, rust, oil, grease, chalk, crayon, paint marks and other deleterious material shall be removed from the interior and exterior surfaces. At the time of shipment, valve shall be clean inside and outside.

      - Inspection and tests

All valves shall be checked for correctness in respect of flange details and face - to - face dimensions. Material test certificates to be provided.

All valves shall be tested hydrostatically for strength, tightness of seats and tightness of back seating at pressures for the full rating of the valve. There shall be no signs of leakage. Water used for hydrostatic testing of valves with stainless steel components shall not have chloride content exceeding 20ppm. Tap water may be used for testing all other valves.

      - Painting and corrosion protection

Unless otherwise specified one coat of primer and two coats of enamel shall be applied to all cast iron exposed surfaces as required to prevent corrosion, after release has been given for painting and before dispatch. All parts shall be adequately protected for rust prevention. The use of grease or oil, other than light grade mineral oil, for corrosion protection is prohibited.

      - Drawings

The Bidder shall furnish, along with his Bid, drawings giving outline dimensions, clearance dimensions for disassembly and weight of valve with actuator if actuator is warranted by size or specification.

      - Name plates

All valves shall have a permanent name plate indicating details as per "Standard marking systems for valves, fittings, flanges and Unions. "In addition, they shall have a permanent stainless-steel tag fixed on the valve body indicating the Purchaser's valve specification tag number or as may be stipulated by Inspecting Engineer.

      - Information to be furnished after the award of contract

The Vendor shall furnish six copies of functional and dimensional drawings for approval.

## Sub-Section - WS - 7

Technical specifications for ductile iron pipes

#### Sub-Section - WS - 7

Technical specifications for ductile iron pipes

Contents

Clause no.			Description				Page nos.

- General

- Ductile iron pipes

    - Applicable codes and standards

    - Fittings, specials and appurtenances

    - Cement mortar linings

    - Design of lining

    - Workmanship

    - Preparation of pipe surface

    - Curing and testing

    - Inspection and remedial work

    - Marking of pipe work

    - Transport and storage

    - Handling

    - Dents and damage

    - Cutting of pipes

    - Pipe laying

    - Fixing expansion joint

    - Backfilling trenches

    - Field hydraulic test

    - External coating

#### Sub-Section - WS - 7: Technical specifications for ductile iron pipes

      - General

  - Scope of work

1.1.1	This specification covers the technical requirements and essential particulars for the supply, manufacture, inspection, erection, testing and cleaning of piping systems as covered in the specification documents and drawings. The CONTRACTOR shall demonstrate that the piping satisfies the requirements of the specification and applicable codes.

1.1.2	This specification covers all details regarding the Ductile Iron Pipe & fittings.

1.1.3	This part of the specification covers the requirements of supply, manufacture, transport, laying, jointing, testing and commissioning of all Ductile Iron pipe lines, above/below ground including civil works for the same.

      - Ductile iron pipes

  - Applicable codes and standards

All piping shall comply with all currently applicable statutes, regulations and safety codes in the locality where the project coming up. The piping shall also conform to the latest editions of the codes and standards listed under below and other applicable standards. Nothing in this specification shall be construed to relieve the CONTRACTOR of this responsibility.

The applicable Indian Standards and codes shall be followed wherever applicable for the Ductile Iron pipes & fittings. In all cases, the latest revision of the standards shall be referred to. If requirements of this specification conflict with the requirements of the standards, this specification shall govern. The following standards, unless otherwise specified herein, shall be referred to.

    - IS: 8329 Specification for Centrifugally Cast (Spun) Ductile Iron Pressure Pipes for Water, Gas and Sewage

    - IS: 9523 Specification for Centrifugally Cast (Spun) Ductile Iron fittings for Pressure Pipes for Water, Gas and Sewage

    - IS: 12288 Code of practice for Use and Laying of ductile Iron pipes

    - IS: 455 Portland Slag Cement

    - IS: 638 Sheet rubber jointing and rubber insertion jointing

    - IS: 1387 General requirements for supply of metallurgical materials

    - IS: 1500 Methods for Brinell hardness test for metallic materials

    - IS: 1608 Mechanical testing of metals - Tensile testing

ii)	IS: 5382 Rubber sealing rings for gas mains, water mains & sewers

- IS: 6452 Specification for high alumina cement for structural use

- IS: 6909 Specification for super sulphate cement

- IS: 8112 43 grade ordinary portable cement

- IS: 11606 Methods of sampling of Cast Iron pipes and fittings

- IS: 12330 Sulphate resisting portable cement

- IS: 13382 Cast Iron specials for mechanical and push on flexible joints for pressure pipe lines for water, gas & sewage

  - Fittings, specials and appurtenances

- General

- . All fittings and special pieces required for curves, tees, branches, air valves, Scour valves, sluice valves etc. shall be suitable for the DI pipes for specified internal diameter and to withstand the specified test pressures.

- The metal used for the manufacture of casting shall confirm to the appropriate grade as per IS 1865. It shall be prepared at the discretion of the manufacturer in a cupola, or an active mixer or other suitable furnace.

- The castings shall be stripped with all precautions necessary to avoid warping or shrinkage defects, detrimental to the good quality. The castings shall be sound and free from surface or other defects.

- Casting showing small imperfections which result from the method of manufacture and which do not affect its final use shall not be rejected on that account alone.

- Minor defects may be rectified with the approval of the purchaser. Repairing of defects by welding, plugging off leaks by caulking or by application of epoxy putty may not be done without previously securing the approval of the purchaser. Any dressing to remove imperfections shall not reduce the thickness of the casting below the specified thickness.

- The castings shall be such that they could be cut, drilled or machined. In case of dispute the castings may be accepted provided that the hardness measured on the external un-machined surface does not exceed 250 HBS.

- Thickness

The thickness 'E' of fittings is calculated as a function of the nominal diameter 'DN' by using the formula given below with the following values for K:

E = K (0.5 + 0.001 DN)

Where K = 14

E = 7 + 0.014 DN

Where K =  12

E = 6 + 0.012 DN

For 'DN 80' the thickness of the fitting has been limited to minimum of 7 mm, so that taking the tolerances into account the thickness of the fittings is always at least equal to that of the pipes of the same nominal diameter.

- Joints

- In the case of push-on-joints for sizes 'DN 600' and above the sockets may be with or without centering rings.

- In case of push-on-joints the spigot end of fitting, if any, shall be suitably chamfered to facilitate smooth entry of spigot in the socket of the pipes or fittings fitted with rubber gasket.

- In case of flange and mechanical joint casting, the flange shall be at right angle to the axis of the joint. The bolt holes shall be either cored or drilled.

- The center bolt holes circle shall be concentric with the bore circle and shall be located off the centerline, unless otherwise specified by the purchaser. Where there are two or more flanges, the bolt holes shall be correctly aligned between them.

- The spigot and socket flexible joint should be designed to permit angular deflection in direction and axial movement to compensate for ground movement and thermal expansion and contraction. They incorporate gasket of elastomeric materials and the joints may be of the simple push-on-type or the type where the seal is effected by the compression of a rubber gasket between a seating on the outside of the socket and the external surface of the spigot. Joints of latter types are referred as mechanical joints.

- Flanged joints are made on pipes having a machined flange at each end of the pipe. The seal is usually effected by means of a flat rubber gasket compressed between two flanges by means of bolts which also serves to connect the pipe rigidly. Gaskets of other materials, both metallic and non-metallic, are used for special applications.

- The flanges can be of adjustable type where the flange comprises of a ring, in one or several parts assembled together, which bears on an end joint hub and can be freely rotated around the pipe axis before jointing.

- Flanges shall be provided at the end of pipes or special where sluice valves, blank flanges, tapers, etc. have to be introduced. The flanged spigot / socket received from the manufacturers will have necessary bolt holes drilled. The Contractor shall assemble the flanged spigot / socket in the exact position so as to get the desired position of the sluice valves, etc. either vertical or horizontal. The drilling pattern shall be matching with the drilling pattern of flanges of valves.

- Blank flanges shall be provided at all ends left unattended for the temporary closure of work and also for commissioning a section of the pipeline or for testing the pipeline laid. For temporary closures, non-pressure blank flanges may be used. For pipes subjected to pressures, the blank flanges or domes suitably designed as per Engineer's requirements shall be provided.

- Jointing procedure

Procedure for jointing will vary according to the type of joint being used. Basic requirements for all types are:

  - Cleanliness of all parts,

  - Correct location of components,

  - Centralization of spigot within socket, and

  - Strict compliance with manufacturer's jointing instructions.

The inside of sockets and the outside of spigots should be cleaned and wire brushed for a distance of 150 to 225 mm. Glands and gaskets should be wiped clean and inspection for damage. When lifting gear is used to place the pipe in the trench, it should also be used to assist in centralizing the spigot in the socket.

Where the pipeline is likely to be subjected to movement due to subsidence or temperature variations, the use of flexible joints is recommended. A gap should be left between the end of the spigot and the back of the spigot and the back of the socket to accommodate such movement.

- Rubber gaskets

The material of rubber gaskets for use with mechanical joints and push-on-joints shall confirm to IS 5382.

- Sampling

Sampling criteria for checking the conformity of the casts shall be as per the IS 9523 & IS 11606.

- Mechanical test

Mechanical test shall be carried out during manufacture by batch sampling system. Samples shall be taken, at the manufacturer's option, from an integrally cast sample, either form a sample attached to the casting or from a sample cast separately. In the latter case, it shall be sent from the same metal as that used for casting. If the casting is subjected to heat treatment as that of castings the samples, being representative of finished product, are tested for tensile strength, elongation and hardness to verify mechanical requirements. One test for castings produced during 24 hours shall be adequate. The results obtained shall be taken as to represent all the fittings of all sizes made during that period.

- Tensile test

One tensile test shall be made on bar cast from the same metal in accordance with the methods specified in IS 1608.

- Hardness test

For checking Brielle hardness specified in 4.5 test may be carried out on the test bar used for the test in 9.1. Test shall be carried out in accordance with the procedures laid down in IS 1500.

- Heat treatment

Fittings shall be supplied in either 'as cast' condition or 'heat treated' condition. In either case, the fittings shall comply with the mechanical properties specified in 9.1 and 9.2. in the case of heat treated fittings the test samples shall be subjected to the same heat treatment process as that of fittings to which they are representative.

- Hydrostatic test

For hydrostatic test, the fittings shall be kept under pressure for 10seconds. They shall withstand the pressure test without showing any sign of leakage, sweating or other defect of any kind. The test shall be conducted before the application of surface coating.

- Tolerances

The tolerance on dimensions of barrel and socket for push on joints fittings shall be as per IS 9523

  - Cement mortar linings

This clause covers the requirement of providing materials and application of cement mortar lining application of Ductile Iron pipes, fittings, specials, etc by centrifugal spinning or by other methods to provide equivalent results.

In case of any discrepancy between this Specification and the standards and codes of practice referred to herein, this Specification shall govern. All standards and codes of practices referred to herein shall be the latest edition including all applicable official amendments and revisions. The following standards and codes are of particular relevance to this work:

AWWA C602-76	Standard for Cement Mortar Lining of Water

Pipelines (4 inches and larger) in Place

IS: 3696	Safety Code for Scaffolds and Ladders (Parts I & II)

ASTM C40	Test for Organic Impurities in Sands for Concrete

The Engineer shall have the right to inspect the source(s) of materials, the operation of procurement and storage of materials, cement mortar batching and mixing equipment and the quality control system. Such inspection shall be arranged and the Engineer's approval obtained prior to starting of any lining work.

- Materials

The cement required for mortar lining shall be Portland Cement conforming to IS: 455

/ IS 269 / IS 8112 or any other type of cement best suited for lining.

To improve workability, density and strength of the mortar, admixtures as approved by the Engineer may be used by the Contractor at his own cost. No admixtures shall be used that would have a deleterious effect on water flowing in the pipe, which is required for drinking purposes. Sand shall consist of inert granular material. The grains shall be strong, durable, and uncoated.

Sand shall not show a colour value (darker than the reference standard colour solution prepared as required by ASTM 640 - Test for Organic Impurities in Sands for Concrete.

Water for mixing mortar shall be clean and free from injurious amounts of mud, oil, organic material or other deleterious substances.

  - Design of lining

The composition of the mortar for the lining shall be cement, sand and water and shall be well mixed to obtain such consistency as to produce a dense, homogenous lining that will adhere firmly to the pipe surface.

The mix proportions of cement and sand shall be 1part cement to 3.5 parts sand by weight. Slight modifications in composition may be made on Site to suit the characteristics of the sand used. Admixtures, if approved by the Engineer, shall be used in strict accordance with the manufacturer's recommendations. The minimum cement content shall be 330 kg/m3.  The soluble chloride ion (Cl) content of the cement of the cement mortar mix shall not exceed 0.15 percent, expressed as a percentage of cement weight.

The water content shall be the minimum that is required to produce a workable mix, with full allowance made for water collecting on the interior of pipe surface.

Cement mortar lining shall have a minimum final thickness of lining shall be as per IS 8329 & IS 9523.

  - Workmanship

All lining work shall be done by machine/hand application. If there are areas where the lining can be done by machine but cannot perform trowel finishing, then the Contractor shall indicate such areas in the method statement submitted as part of his bid. By prior approval of Engineer, these areas may be machine sprayed and hand trowelled.

The plant and equipment proposed by the Contractor for carrying out the cement mortar lining application shall be approved by the Engineer.

  - Preparation of pipe surface

The interior surface of pipe to be lined shall be cleaned to remove all rust, chemical or other deposits, loose and deteriorated remains of old coating materials, oil, grease, and all accumulations of water, dirt, and debris. The cleaning of the surface shall be carried out by the use of suitable chemical or mechanical means with the approval of Engineer. The extent of cleaning shall be to the satisfaction of the Engineer.

All loose mill scale, dirt, rust, and accumulation of construction debris shall be removed from the interior surface of the pipeline. The pipeline shall be cleaned by use of power-driven cleaner incorporating revolving brushes on rotating arms. After this cleaning the pipe shall be flushed with potable water and all standing water removed.

Immediately prior to the travel of the lining machine through the pipeline, all foreign material shall be removed. This includes sand and loose mortar that might have accumulated since the work of preparation of surfaces was completed.

  - Curing and testing

Pipe sections may be moved to a curing area immediately after completion of the mortar lining and hand finishing of a section of pipeline. Care shall be exercised at all time to prevent damage to the lining. At the option of the manufacturer, linings shall be either accelerated cured or moist cured.

On arrival at the curing area, but not later than 30 min after completion of the lining operation, pipe ends shall be covered with plastic or wet burlap for a minimum period of 24 hour before applying the exterior coating. The lining shall be cured for a total period of four days before shipment. The ends of the pipe sections shall be kept closed during the curing period, with plastic end caps except when sprinkling hands are used. The reinforcement and outside coatings are being applied or accelerated curing is being substituted. Care must be taken by the manufacturer to avoid drying to or cracking of the lining.

The pipes shall be cured at temperatures greater than 4° C. Any loss of water from the mortar by evaporation shall be sufficiently slow so that hardening is not impeded.

Test blocks of the same material as used for the lining shall be made in 150 mm cube moulds and subjected to Works cube crushing tests. Each block shall be removed from its mould as soon as practicable and cured under the conditions of temperature and humidity identical with those in which the lining of the pipe is cured. The number of tests shall be at least 4 cubes for each age and each water cement ratio. The works cube strength of the test cube shall not be less than 300 kg/cm2 after 28 days of curing or 170 kg/cm2 after 7 days of curing. The density of the test cube shall not be less than 2300 kg/m3.

A set of minimum two test cylinders, 50 mm in diameter by 300 mm in length shall be made each day. The test cylinders shall be cured with the pipe at the same temperature and for the same total length of time. Other sizes cylinders, such as 50 mm x 100 mm may be used to test compressive strength.

The manufacturer may use centrifugally spun test cylinders. Test cylinders shall be spun about their longitudinal axes in 150 mm diameter by 300 mm long steel molds at a speed that will simulate the compaction of mortar in the lining to produce a spun cylinder wall thickness of at least 35 mm. The net cross sectional area of the hollow cylinder shall be used to determine its compressive strength. Damaged cylinders shall not be tested.

Minimum compressive strength should be of 7 MPa in 7 days and 31 MPa in 28 days. Pipe made with mortar lining does not meet the strength requirements set forth above shall be subject to rejection.

The average of 10 consecutive strength tests of cylinder representing each mortar mix shall be equal to or greater than specified strength and not more than 20 percent of the strength tests shall have values less than the specified strength. No cylinder test result shall be less than 80 percent of the specified strength.

  - Inspection and remedial work

The entire procedure of applying cement mortar lining shall be subject to continuous inspection by the Engineer but such inspection shall not relieve the Contractor of his responsibility to, furnish material and perform work in accordance with this specification. All cement mortar lining not applied in accordance with this specification, shall be subject to rejection by the Engineer. Lining so rejected shall be removed and replaced by the Contractor at his own expense.

Defects in lining including but not restricted to sand pockets, voids, over sanded areas, blisters, cracked and dummy areas, and thin spots shall be removed, and the area shall be repaired by hand application to the full required thickness of the mortar lining. Defective areas encompassing the full diameter of the pipe shall be replaced by machine wherever practical. Defective lining rejected at the time of lining shall be removed before initial set of the mortar. Defective lining rejected after initial set shall be replaced or repaired by the most practical method as determined by the Engineer.

  - Marking of pipe work

The component parts of the pipes shall be carefully marked for identification in the field. The marking shall be on the side which will be the inside of the pipe after bending. The marking operation shall be conducted with full size rulers and templates. Only blunt nose punches should be used.

After the hydraulic tests on the specials and other items, the number of the shell in the line as it will be erected and the direction or flow shall be stamped in a prominent manner on each piece.

A register shall be maintained in suitable pro-forma giving the following information for each shell tested

- Serial No.

- Shell No.

- Date of test

- Thickness and specification of pipe

- Weight of shell tested

- Maximum test pressure

- Details of test performance

- Details of radiographic examination of welds

  - Transport and storage

All pipes and specials manufactured in the factory and temporarily stacked in the Contractor's yard shall be transported to the site of laying after cleaning them internally. The item of transport covers the cost of loading in the factory, transporting to the site of laying or to stacking yard selected by the Engineer in its vicinity and unloading and stacking them carefully in such a manner that the material so kept is not easily disturbed or rolled away from the place of stacking. The loading in the factory shall be carried out by means of either a crane, gantry or shear legs, so as not to cause any damage to the finished material. Similarly, while unloading and stacking, great care shall be taken to ensure that the material is not damaged or dented. The material stacked at site shall be jointly inspected by the Engineer and the Contractor and defect or damage noticed shall be repaired to the satisfaction of the Engineer before payment is admitted.

Props of approved designs shall be fixed to the pipes during transit to avoid undue sagging and consequent distortion. After the pipes are carefully stacked, props may be removed and re-used for subsequent operations. The stacking ground, both in the Contractor's yard and at the site of laying shall be selected in such a way as not to get waterlogged during monsoon. If this cannot be done, the pipes shall be supported on sleepers to avoid contact with wet earth and subsequent rusting. In order to prevent sagging during transit, savings of steel plates can be utilized by cutting to the required length and tacking the same to the pipe ends, in place of props, if approved by the Engineer.

As explained in earlier paragraphs, materials such as pipes, tapers, etc. may be transported to the site of laying as soon as the material is finished in all respects with the permission of the Engineer to avoid congestion in the Contractor's yard. However, materials such as expansion joints, composite bends, 'T' branches and other similar parts shall be stacked in the Contractor's yard until they are required for laying in the field. In view of this, the work of fabrication of such materials shall be properly synchronized as far as possible with the laying operations.

Fabricated materials such as manhole covers, appurtenances, bolts, nuts, distance pipes, flanges, saddles, collars bypass arrangements etc. shall be transported to the site of laying from the fabrication shop according to the needs of the laying operations only.

To ensure that the work of erecting pipes is not held up at any stage and place, the Contractor shall maintain an adequate stock of standard specials, flange rings, plug plates, short length of smaller diameter pipelines, etc. at site in his field stores, in consultation with the Engineer. Wherever possible, the Contractor shall arrange one full month's requirement of pipes, specials, etc. stacked along the alignment.

Padding shall be provided between coated pipes and timber skids to avoid damage to the coating. Suitable gaps in the pipes stacked shall be left at intervals to permit access from one side to the other. The pipes, specials, appurtenances so received on site shall be jointly inspected and defects recorded, if any, such as protrusions, grooves, dents, notches, damage to the internal coating etc. shall be pointed out immediately to the Engineer at the site and in the acknowledgement challans. Such defects shall be rectified or repaired to the satisfaction of the Engineer entirely at the Contractor's risk and cost.

  - Handling

It is essential to avoid damage to the pipes, fittings and specials or their coatings. At all stages during handling. The pipes and specials shall be handled in such a manner as not to distort their circularity or cause any damage to their surface treatment. Pipes shall not be thrown down from the trucks nor shall they be dragged or rolled along hard surfaces, slings of canvas or equally non abrasive materials of suitable width of special attachment shaped to fit the pipe ends shall be used to lift and lower coated pipes to prevent damage to the coating.

Great care shall be taken in handling the pipe right from the first operation of manfacture until they are laid and jointed. The Contractor shall provide temporary props in order to prevent any sagging of the pipes while they are stacked in their yard and while transporting to the site of delivery, i.e. laying. The props shall be retained until the pipes are laid. If at any time these props are found to be dislodged or disturbed, the Contractor shall immediately reinstate them in such a way that the true shape of the pipe shell or specials is maintained to the satisfaction of the Engineer. No defective or damaged pipe or special shall be allowed to be used in the work without rectification to the satisfaction of the Engineer. Any damage to the coating shall be repaired by the Contractor at his own cost to the satisfaction of the Engineer.

Coated pipes and specials that are to be stored on supports shall bear on the uncoated ends only. If bearing on coating is employed the supports shall be not less than 200 mm wide and so arranged to prevent damage to the coating.

During handling of the pipes and fittings, coating shall be protected not less than 200 mm wide and placing strips of heavy belting or other approved sheet materials not less than 200 mm wide under all ropes or fastening.

  - Dents and damage

Whenever any dent, i.e. a significant alteration of the curvature of the pipe shell is noticed, the depth of the dent shall be measured between the lowest point of the dent and the pipe shell curvature line. Cutting out a cylindrical portion of the pipe and replacing the same by an undamaged piece of the pipe shall remove all dents exceeding 2 percent of the outer diameter of the pipe. The Engineer may permit insert patching if the diameter of the patch is less than 25 percent of the nominal diameter of the pipe. Repairs by hammering with or without heating shall not be permitted.

Any damage to the coating shall also be carefully examined and rectified.

  - Cutting of pipes

The cutting of pipe for inserting valves, fittings, etc, shall be done in a neat and workman like manner without damage to the pipe or lining so as to leave a smooth end at right angles to the axis of the pipe.

Methods of cutting

By hacksaw

Hand or Power operated hacksaw should be used with blades having teeth at a pitch of mm.

By manually operated wheel cutter

The type of cutting wheel used for cast iron pipes is not suitable for ductile iron pipes. Special Wheels, as used for cutting steel pipes shall be used and cut ends are trimmed with a file.

By pipe cutting machine

Machines with cutter heads or abrasive wheels shall be used. Cutter head should have a front rake angle of 7° as used for steel pipes.

  - Pipe laying

Unless specified otherwise, the pipeline shall be erected on saddles or laid on granular bedding. Only material approved by the Engineer shall be used. The Contractor shall equip himself with all necessary tools, machinery, labour etc. required for the purpose.

No work shall be done in the absence of Contractor's Engineer, either during the daytime or at night.

The components of the pipe work have been so designed that the corresponding joints, holes, edges etc shall coincide at the mean temperature. All works such as fixing flanges, base plate etc. in true alignment and in correct position and tack welding pipes shall therefore be done at the mean temperature. The temperature shall be ascertained by means of mercury cups fixed to the pipe shell from outside and thermometers of the required type and range.

The relevant provision under welding such as qualification standard for welding procedures, tests on welder's work and removal of defects etc., shall also apply to in- situ welding.

Pipe laying for river/canal crossings shall generally start from the fixing points on either side, the expansion joints being provided last. Fixing points shall be at all anchor blocks.

The owner shall construct anchor blocks before commencing the pipe laying work in any section. The construction of the blocks shall be carried out in 3 stages:

- The lower part up to 150 mm below the invert of the pipeline, including concrete support chairs, shall be constructed;

- The pipeline on this part of the block shall be laid;

- The remaining block around and over the pipeline shall be constructed.

The saddles along with the embedded stainless steel plate shall be cast at least 3 weeks before the pipeline is laid on them. After all saddles between successive fixity points have been cast. A line plan showing the actual position thereof shall be prepared, after taking levels and measuring distances. In case of any errors in casting the pedestals, corrections shall be applied. The pipe laying work shall then start from the fixity points and shall proceed towards the expansion joints. The Contractor shall determine the method of jointing the pipes and erecting them on previously cast reinforced concrete saddles.

The pipe strakes shall be assembled in position on the saddles by the equipment approved by the Engineer. Normally, not more than two pipes shall be aligned, tacked and kept in position on temporary supports. The Contractor shall not proceed with further work, until the circumferential joints of these pipes are fully welded. During assembly, the pipeline shall be supported on wooden sleepers and wedges, with the free end of the pipe jne held in position by slings to avoid deflection due to temperature variations during the day. In general, the assembly of pipe strakes and one run of welding shall be done during the day time while full welding including the external gouging and sealing runs shall be done after 5.00 PM. The Contractor shall maintain the continuity of the work by adding two more pipes on the second day in a similar manner, after full welding of the previous joints is completed during the night while this new work is being done, the Contractor shall proceed with the work of providing permanent supports for the pipeline assembled and welded previously.

Where specified, a granular bedding of the required thickness and level shall be provided below the pipe prior to laying the pipe in the trench. The bedding shall be compacted with a light hand rammer, and any reduction in thickness due to compaction shall be made up by adding sand during ramming.

Pipes should be lowered into the trench with tackle suitable for weight of pipes. For smaller sizes, up to 250 mm nominal bore, the pipe may be lowered by the use of ropes but for heavier pipes, either a well designed set of shear legs or mobile crane should be used. When lifting gear is used, the positioning of the sling to ensure a proper

balance should be checked when the pipe is just clear of the ground. If sheathed pipes are being laid, suitable wide slings or scissor dogs should be used.

When the pipeline laid underground or above ground in a long narrow cutting gets submerged in water collected in the trench of cutting it is subjected to an uplift pressure due to buoyancy and is likely to float if completely or partly empty. In the design of pipelines, provision is made to safeguard against floatation providing sufficient overburden or by providing sufficient dead weight by means of blocks, etc.

The Contractor shall see that the water shall not be allowed to accumulate in open trenches. Where work is in an incomplete stage, precautionary work, such as blank- flanging in the open ends of the pipeline and filling the pipeline with water etc. shall be taken up as directed by the Engineer.

Protection of the pipeline against floatation during the Contract Period shall be the responsibility of the Contractor. Should any section of the pipeline float due to his negligence, etc. the entire cost of laying it again to the correct line and level shall be to his account.

The progress of pipe laying shall follow the detailed programme submitted by the Contractor with his bid and confirmed and updated at the start of construction. The Contractor shall programme his activities such that the laying of pipes follows closely the manufacturing schedule and no pipes remain stacked in the factory or at Site for a period of more than two months.

  - Fixing expansion joint

The work of laying pipeline as a rule starts from the fixity points and proceeds towards the expansion joints. It shall be continued until the gap between the pipe ends is less than the lengths of the expansion joint plus pipe strake length. At this stage, the exact gap between the pipe ends shall be measured at mean temperature of that locality. Let it be 'X', Similarly, the exact length of the pipe strake and the expansion joint bought at site shall be measured at the same, temperature let these be 'Y' and .Z' respectively. Normally, the length of the expansion joint ('Z') is standard.

Case when 'y' plus 'Z' is more than 'X' or equal to 'X' (i.e. fixing of expansion joint without strip)

- At mean temperature the exact gap between pipes shall be measured. Free ends of pipes shall be brought in a correct line and level; lateral movement, if any, shall be corrected. Then the gap between the free ends shall be made equal to the exact length of the expansion joint by cutting one of the pipe ends. Choice of the end to be cut must be made from the point of view of bringing the expansion joint to a central position.

- The expansion joints are normally supplied without packing. The normal length of the expansion joint shall be reduced by about 100 mm by cutting the inside locks, and inserting the inner strake by means of turnbuckles. At mean temperature this expansion joint shall be inserted inside the gap (care being taken to keep the tapered portion on the down-stream side), and both ends shall be tack welded to the pipe ends, after pulling the expansion joint. (Tacks of these two joints shall be of longer length. Approximately 100 mm long).

- Welding of these two joints of the expansion joints shall be started only after it is ascertained by taking observations that the expansion joint is functioning properly. The procedure to be followed for taking observations is given in item (2.2.1.4) of this clause.

- Case when 'Y' plus 'Z' is less than. Xi (i. e. fixing of expansion joints with strap):

  - The expansion joint shall be laid in locked position. Before laying the pipes adjacent to the expansion joint, the exact gap between the pipes shall be calculated by taking measurements of the first pipe (upstream of the expansion joint), and the second, pipe (downstream of the expansion joint) at Mean Temperature.

  - If the gap is less than 100 mm, the second pipe shall be cut to make the desired gap of at least 100 mm. If the gap is more than 200 mm, suitable distance piece of not less than 600 mm shall be inserted after cutting necessary length of the first pipe.

  - The second pipe shall then be laid in position. Then a strap of length equal to three times the gap length shall be welded to the pipe, overlapping the second pipe by the gap length. The other end of the strip shall be kept free.

  - At mean temperature the-.other end of the strap shall be tacked to the first pipe, after checking of the line and level. Simultaneously, all the locks of the expansion joint shall be removed and chipped off properly.

  - Welding of the joints between the strap and the first pipe shall be started only after observations are over and it is ascertained that the expansion joint is functioning properly.

- Observations

- Before fixing the expansion joint, two mercury cups one on the left and the other on the right side shall be fixed on the pipe near the upstream side of the expansion joint.

- Immediately after the expansion joint in case (a) above or the strap in case

(b) above is tack welded, observations for total expansion or contraction shall be started and continued for 48 hours round the clock. Similarly, the central and end fixity pedestals shall be kept constantly under observation.

- The expansion and contraction shall be measured by making a temporary marking on the inner strake (on the upstream side) and measuring the distance between this mark and the edge of the gland of the expansion joint.

  - Backfilling trenches

The trench shall be filled with selected material up to 300 mm above the pipes. This backfill shall be provided in layers not more than 150 mm, with a density more than 95% of standard proctor density. Samples shall be tested as directed by the Engineer. The remaining depth of trenches shall be filled with ground backfill material.

Refilling of trenches shall be started by the contractor with a view of restricting the length of open trenches. Pipe laying shall closely follow the progress of trench excavation. If the Engineer considers that the contractor is not complying with any of the foregoing requirements, he may prohibit further trench excavation until he is satisfied with the progress of laying and testing of pipes and refilling of, trenches, care shall be taken during backfilling, not to injure or disturb the pipes, joints or coating. Filling shall be carried out simultaneously on both sides of the pipes so that unequal pressure does not occur. Walking or working on' the completed pipeline will not be permitted unless the trench has been filled to height of at least 300 mm over the top of the pipe except as may be necessary for tamping etc. during backfilling work. The backfilling shall be done in accordance with Specifications given elsewhere in this report.

To prevent buckling of pipe shell of diameters 1200 mm and above, pipes shall be strutted from inside while the work of refilling is in progress, for which no separate payment shall be made.

For pipelines of diameters below 1200 mm strutting shall be done from inside at either end of the stretch of the pipeline under refilling, by means of strong spiders which shall be sufficiently stiff to resist all deformation for which no extra payment will be made.

Strutting shall be done by means of strong spiders having at least 6 arms which shall be sufficiently stiff to resist all deformation. Spiders shall be provided at a maximum interval of 2 m.

The Engineer shall at all times have powers to decide which portion of the excavated materials shall be for filling and in which portion of the site and in what manner it shall be so used.

If suitable material for refilling is not available for excavation the Contractor shall bring earth, murrum of approved quality as directed by the Engineer.

Regular measurement of the field dry density shall be taken by the Contractor at various levels in the backfilling as required by the Engineer.

No mechanical plant other than approved compacting equipment shall run over or operate within the trench until backfilling has reached its final level or the approval of the Engineer has been obtained.

  - Field hydraulic test

After erection at site and after the Concrete anchor blocks have been constructed but prior to internal painting, the entire pipeline shall be subjected to a hydraulic test as follows:

- The test pressure shall be minimum of 1.5 times the working pressure, but not to exceed a pressure that would result in a stress greater than 80% of the yield point.

- The pressure test shall be conducted in dry weather with pressure held constant for 24 hours to observe whether any pressure drop takes place. The test pressure shall be gradually raised at the rate of 0.1 N/Sq.mm per minute. A leakage of 0.1 litre per mm diameter of pipe per kilometre length per 30 m head test pressure per 24 hours is allowed if the test pressure is maintained by pumping. Any leakage beyond that specified herein above shall be rectified to the satisfaction of the Engineer.

- During the test, the pipe shall be struck sharp blows with 1 kg hammer. Water shall not spout, ooze or sweat either through joints-welded or bolted or the body of the pipe. If any leakage noticed, shall be repaired by the Contractor, which shall include coating and repairing of the damaged portion. The Contractor at his own cost shall carry out repairs and replacements and further testing including the cost of the plates and other raw materials.

  - External coating

- Zinc coating

Pipe surface condition

The pipe surface shall be dry and free from rust or any non-adhering particles or foreign matter such as oil or grease. Metallic zinc shall be applied on to the oxide external surface of the pipe.

Materials

The coating materials are metallic zinc with content of at least 99 percent by mass.

Method of application

The metallic zinc coating shall be applied by a spraying process in which metallic zinc material is heated to a molten state and projected in small droplets by spray guns onto surface. The zinc rich paint coating shall be applied by a spraying or a brush process onto the pipe surface in case of repair only.

Coating characteristics

The metallic zinc coating shall cover the outside diameter of the pipe and shall be free from such defects as bare patches or lack of adhesion, Damaged areas or zinc coating caused by handling arc acceptable provided that the damage is less than 5 cm2/m2 of coated Surface and provided that the minor dimensions of the damaged area do not exceed 5 mm.

Zinc coating mass

The average mass of zinc coating shall be not less than 130 g/m2 with a local minimum of 110g/m2.

Determination of zinc coating

Manufacturing process control system shall specify the frequency of this test. A rectangular token is attached along the pipe axis before passing it through the zinc coating equipment, after coating and trimming the minimum token sizes shall be either:

- 250 mm x 100 mm, or

- 500 mm x 50 mm.

Repairs of the zinc coating

Areas left uncoated, for example under the test token and coating damaged in excess of 5 cm2/m2 or coating shall be repaired by either:

- A metallic zinc sprays.

- By application of zinc rich paint containing more than 90 percent zinc by mass in the dried film: mean mass of the applied paint shall not be less than 150 g/m2.

- Flanges of welded flanged pipes and welded parts of the flanges shall be coated with zinc rich paints (90 percent).

Finishing layer

After metallic zinc coating or zinc rich paint coating the pipe shall be given a finishing layer of bituminous paint or synthetic resin compatible with the zinc coating. Application of this finishing layer may be done by any proven process such as spraying or brush coating at the manufacturer’s choice. It shall uniformly cover the zinc coating and be free from bare patches or lack of adhesion. The mean dry film thickness of the finishing layer shall not be less than 70~m with nowhere less than 50 µm.

##### Bituminous coating General

Unless otherwise agreed between the purchaser and Manufacturer, all pipes shall be coated externally and internally with the same material, (Bituminous coatings are either hot applied or cold applied,)

General characteristics

Coating shall not be applied to any pipe unless its surfaces arc clean, dry and free from rust.

Unless otherwise agreed between the purchaser and the manufacturer all pipes shall be coated externally and internally with the same material. The method of coating shall be as per usual practice of the manufacturer. The coating material shall set rapidly with good adherence and shall not scale off. The mean thickness of the coating shall be not less than 70 µm and the local. Minimum thickness shall be not less than 50 µm.

Where the coating material has a bitumen base, it shall be, smooth and tenacious and hard enough not to flow when exposed to a temperature of 65°C but not so brittle at a temperature or 0°c as to chip off when scribed with a penknife.

When the pipes arc to be used for conveying portable water the inside coating shall not contain any constituent soluble in such water or any ingredient which could impart any taste or whatsoever to the portable water after sterilization and suitable washing of the mains.

Pipes with or without sockets and flanges, which are imperfectly coated, or where the coating does not set or conform to the required quality, the coating shall be removed and the pipes/flanges recoated.

##### Polyethylene sleeving Material

Characteristics

The material used for making the film is polyethylene or a mixture of polyethylene or a mixture of polyethylene and /or	ethylene and olefin copolymers.

Its density shall be between 910 and 930 kg / m3

Additives and impurities

If protection against ultra - violet rays is required, the material shall be stabilized by the addition of an appropriate product: if carbon black is used for this purpose the addition shall be in the range of 2 to 3 percent by mass.

Dimension Width

The normal flat width of the tube or flat or flat sheet is specified in Table 34.

Thickness

The normal thickness of the sleeving shall be not less than 200 µm and not more than 250 µm unless otherwise agreed.

The negative tolerance on the nominal thickness shall not exceed 10 percent.

If necessary, it is permitted to use thicker sleeving or double sleeving.

Mechanical properties

Tensile strength of the film in the longitudinal and transverse direction shall not be less than 8.3 MPa.

Elongation

The elongation at fracture of the film in the longitudinal and transverse directions shall not be less than 300 percent.

Dielectric strength

The dielectric strength of the film should be 31.5V/µm minimum.

Annexure - B

Frequency of sampling and testing

Table 1: Frequency of sampling and testing

| Sl. No. | Nature of test/ characteristics | Methods of test | No. of samples & frequency of test | Remarks |
| --- | --- | --- | --- | --- |
| I. | Suitability of fill materials |  |  |  |
|  | (a) Grain size analysis | IS:2720 (Part-IV) | One in every 2000 Cum. for each type and each source of fill material subject to a minimum of | Test for and sand |
|  | (b) Liquid limit and plastic limit | IS:2720 (Part-V) | two samples | Test for soil |
|  | (c) Shrinkage limit | IS:2720 (Part-VI) | One in every 5000 cum. for each type | The frequency of Test shall be |
|  | (d) Free sweel index | IS:2720 (Part-XL) | and each source of fill materials. | increased depending on type of soil |
|  | (e) Chemical Analysis | IS:2720 |  |  |
|  | i. Organic matter | Part XXII | One in every 5000 Cum for each type and each source of | Test for sand and soil. |
|  | ii. Calcium carbonate | Part XXIII | fill materials. |  |
|  | iii. pH | Part XXVI |  |  |
|  | iv. Total soluble sulphate | Part XXVII |  |  |
| II. | Standard proctor test | IS:2720 (Part VII) | One in every 2000 cum. for each type and each source of fill materials | Test for soil for determining optimum moisture content, Dry Density etc. |
| III. | Moisture content of Fill before compaction. | IS:2720 (Part II) | -do- | Test for soil |
| IV. | Degree of compaction of fill |  | (i) For foundation filling, one for every ten foundations for each | Test for soil |
|  | (a) Dry density by core cutter method | IS:2720 (Part XXIX) | Compacted layer. However, each layer for location of important and heavily loaded |  |
|  | or |  |  |  |
|  | Dry density in place by sand displacement method | IS:2720 (Part XXVIII) | Foundations resting on fill shall be tested. |  |
| Sl. No. | Nature of test/ characteristics | Methods of test | No. of samples & frequency of test | Remarks |
|  |  |  | (ii) For area filling one for every 1000 Sqm. area for each compacted layer. |  |
|  | (b) Relative density index | IS:2720 (Part XIV) | -do- (i) & (ii) | Test for sand |
|  | (c) Dry density by proctor needle penetration | Standard Practice | Random checks to be carried out for each compacted layer in addition to tests mentioned under IV (a) above. | Test for soil |

# Annexure - C

List of tender drawings

# Annexure C - List of drawings

| Sl. No. | Drawing No. | Drawing title |
| --- | --- | --- |
| 1) General |  |  |
| 1 | MWC – IWTP - G- 001 | Index Map |
| 2 | MWC – IWTP - G- 001 | Head Work |
| 3 | MWC – IWTP - G- 001 | Pumping Main Alignment |
| 4 | MWC – IWTP - G- 001 | Existing WTP Process |
| 5 | MWC – IWTP - G- 001 | Existing WTP Layout |
| 6 | MWC – IWTP - G- 001 | Existing WTP P&I Diagram |
| 7 | MWC – IWTP - G- 001 | Proposed WTP Process Improvements |
| 8 | MWC – IWTP - G- 001 | Proposed WTP Layout Improvements |
| 9 | MWC – IWTP - G- 001 | Proposed WTP P&I Diagram |
| 10 | MWC – IWTP - G- 001 | G.A. of BAS TANK |
| 11 | MWC – IWTP - G- 001 | G.A. of Wastewater Collection Tank |
| 12 | MWC – IWTP - G- 001 | G.A. of Centrifuge Feed Pump Pit |