VOLUME II – A- Part 4

Technical Specification

Operation and Maintenance works

Contents

1.	INTRODUCTION	3

2.	GENERAL SCOPE	3

3.	START OF O & M PERIOD	6

4.	GENERAL REQUIREMENTS FOR O & M	7

4.1.	Performance Standards	10

5.	INSTRUCTION MANUALS, “AS MADE” DRAWINGS	12

6.	TESTING AND ANALYSES DURING O & M	14

7.	MINIMUM MAINTENANCE REQUIREMENTS	14

8.	MAINTENANCE OF ELECTRICAL SYSTEM	15

9.	MAINTENANCE OF TREATMENT PLANT AND OTHER ASSOCIATED WORKS	16

10.	MAINTENANCE OF DIESEL GENERATOR	16

11.	PREVENTIVE MAINTENANCE	17

12.	FAILURE REPORTS	20

13.	PLANT AND ASSOCIATED WORKS OPERATION AND MAINTENANCE REPORT	20

Section-4:	Technical Specification for Operation and Maintenance of the Project

INTRODUCTION

The Contractor shall ensure the Operation and Maintenance of the Water Treatment Plant and Intake Well in compliance to the appropriate guidelines contained in this document.

The Contractor shall be responsible for the operation and maintenance of the Water Treatment Plant as described in the Operations and Maintenance Specifications. The Contractor shall manage, operate and maintain the Water Treatment Plant and supply treated water of quantity and quality specified in this document.

GENERAL SCOPE

- Pumping and transmitting the raw water from existing Intake well to the water treatment works;

- Treating the raw water to the stipulated Potable Water Specification;

- Sampling raw water at the point it enters the WTP to check whether it meets the limits of raw water quality characteristics detailed in the Raw Water Analysis Report provided in Volume IIA – Part1 – Clause 3.8.1: Design Responsibilities;

- Sampling treated water as it leaves the water treatment works to ensure that it meets the Potable Water Specification Volume IIA – Part1 – Clause 3.8.1: Design Responsibilities; and

- The Contractor shall operate and maintain the WTP to deliver water as specified to the levels under the Contract, complete including the civil/structural, mechanical components, instrumentation system, and electrical system, all utility and ancillary buildings for the period of seven (7) years from the date of issuance of Commissioning Certificate.

- The Contractor shall comply with all safety rules and regulations as specified by the MWC as referred in Contract.

- The Contractor shall make his own arrangements at his own cost for Works operation, personnel, lubricants, spares, tools and tackles, routine maintenance, and any other activity required for the operation and maintenance of the WTP.

- Carrying out regular flow measurements and recording of treated water at Delivery Point.

- Prepare Standard operating procedures and operations & maintenance manuals for all components of the project / installations;

- Engage and train the staff appointed by MWC in the operation and maintenance of the Works;

- Collecting samples of Raw water as well as treated water and analyzing / testing the water samples in the In-house Laboratory and NABL accredited Laboratory for the following parameters with minimum frequency as specified below: -

| Sr. No. | Parameter to be Tested | Raw Water (at Collection Well) |  | Treated Water (UF/MF Permeate) |  |
| --- | --- | --- | --- | --- | --- |
|  |  | To be Tested (Y/N) | Frequency | To be Tested (Y/N) | Frequency |
| 1. | Turbidity | Y | Daily | Y | Daily |
| 2. | pH | Y | Daily | Y | Daily |
| 3. | Total Suspended Solids | Y | Daily | Y | Daily |
| 4. | Total Dissolved Solids | Y | Daily | Y | Daily |
| 5. | Total Alkalinity | Y | Daily | Y | Daily |
| 6. | Total Hardness | Y | Daily | Y | Daily |
| 7. | Calcium | N | -- | Y | Weekly |
| 8. | Chloride | Y | Weekly | Y | Weekly |
| 9. | Residual Chlorine | N | -- | Y | Daily |
| 10. | Fluoride | Y | Monthly | Y | Monthly |
| 11. | Nitrate | Y | Monthly | Y | Monthly |
| 12. | Sulphate | Y | Weekly | Y | Weekly |
| 13. | BOD | Y | Weekly | Y | Weekly |
| 14. | COD | Y | Daily | Y | Daily |
| 15. | Total Coliform bacteria | N | -- | Y | Daily |
| 16. | E. Coli | N | -- | Y | Daily |
| 17. | Iron | Y | Monthly | Y | Monthly |
| 18. | Copper | Y | Monthly | Y | Monthly |
| 19. | Zinc | Y | Monthly | Y | Monthly |
| 20. | Cadmium | Y | Monthly | Y | Monthly |
| 21. | Chromium | Y | Monthly | Y | Monthly |
| 22. | Lead | Y | Monthly | Y | Monthly |
| 23. | Arsenic | Y | Monthly | Y | Monthly |
| 24. | Nickel | Y | Monthly | Y | Monthly |
| 25. | Selenium | Y | Monthly | Y | Monthly |
| 26. | Mercury | Y | Monthly | Y | Monthly |

Note:

(i) The Bacteriological quality of treated water will be tested daily with the help of H2S Kits and if sample found contaminated, shall be sent to the laboratory for testing by MPN Method. All Heavy metals shall be tested in NABL accredited laboratory.

- Take all necessary measures to minimize the power consumption in carrying out its operations.

- Operate electrical equipment during power failures by making appropriate alternative arrangements.

- The Contractor shall submit detailed schedule/manual of all O&M activities with references of equipment manufacturers’ maintenance schedules/manuals to the MWC for review and approval.

- The Contractor shall submit Guidelines and Instructions manual for the maintenance staff of all levels for all the spares, tools, plants and equipment and WTP/pumping stations under the Water Treatment System to maintain the service levels within the standards prescribed in the Contract;

- The Contractor shall carry out all O&M activities to meet the key Performance Standards as per the approved Operation and Maintenance Manuals.

- The Contractor’s responsibility shall also include the safety and security of the Works during the course of Operation and Maintenance.

- Acquire and maintain sufficient stock of consumables required to operate the Water Treatment System in accordance with good practices and applicable standards and procure necessary electrical and mechanical equipment required for operations and maintenance of Water Treatment System to ensure continuous operations.

- Establish a Project office to manage the Project. The Project office can be located at the water treatment plant campus.

- During Operation and Maintenance period, the Contractor shall appoint suitable number of technical staff, Contractors, fitters, electricians, helpers, as required for the operation and maintenance of complete proposed Water Treatment System including the WTP for three shifts and adequate other staff / supporting personnel during general shift for security of man-power, built structures, equipment and other system components. The Contractor shall make the arrangement of reliever for weekly off/holiday etc. Absence on any grounds like weekly off or holiday shall not be considered. The presence of staff in each shift should be marked in  Contractor employee attendance register to be maintained at office of Shift in charge at Water Treatment Plant that shall be considered as final.

- The Contractor shall have to issue identity cards with photographs to all the staff employed for Operation and Maintenance as per the Labor Act. The list of the same shall be submitted to the MWC mentioning qualification & experience.

- The MWC will not be responsible for any accident /injury to the staff of the Contractor. Further the MWC will not provide any insurance or medical facility to the staff of Contractor. The responsibility lies with the Contractor.

- All Central / State Government / Semi-Government / Appropriate Regulator / Local Body’s Rules and Regulations pertaining to this contract shall be followed and observed by the Contractor without any extra cost to the Employer. No watch and ward, safety insurance, security, storage, housing accommodation etc. will be provided by MWC. This will be responsibility of Contractor.

- No accommodation / guesthouse / transportation facility will be provided by the MWC to the Contractor.

- Unsatisfactory and inefficient running of the Water Treatment System and unnecessary and excessive usage of power, spare, consumable, etc. supported by the reasons which are under control of Contractor will be highly objected. In such cases MWC’s Representative’s decision will be final and binding on the Contractor.

- The Contractor will be required to maintain the required power factor for the operation of the components of the Water Treatment System including the WTP as prescribed by the applicable guidelines and authority in Tamil Nadu. In case any penalty is levied on the MWC for not maintaining the power factor, this will be recovered from the Contractor.

- Variability of throughput: If the quantity of treated water can be decreased in the existing system without impacting the annual fixed costs to the Contractor, the Contractor shall comply with such requirements.

- Draft O&M Plan

Within 30 days before issue of Commissioning Certification, the Contractor shall prepare an annual operating & maintenance plan comprising of the operating and maintenance strategy for maintaining operating efficiency, methodology, organization structure, human resource plan, equipment deployment plan, environmental management measures, responsibilities for unit operations, monitoring and emergency response, related processes, systems, protocols, procedures including detailed costs for each activity of operations and maintenance etc. as per CPHEEO latest Manual on Water supply.:

O&M Plan will present in detail the monitoring protocol for water quality measurement around the system. This protocol will cover the whole process from designing the sampling regime, taking samples, testing samples, and reporting samples. The O&M Plan will also present the on-line water quality reporting system required to meet the Service Levels.

- Output and Operational Guarantees

The Contractor is fully responsible for meeting the product water quantity of 4.5 MLD and quality as prescribed above.

START OF O & M PERIOD

The period will commence 15 days after trial run. The MWC shall not delay the start of the Operation and Maintenance Period contemplated by this Clause on account of minor deficiencies of materials or defects in the Plant and Project which do not in any case affect the ability and performance of the Plant and Project to produce the required product water, provided that the Contractor shall undertake to repair the minor deficiencies within 14 days. Operation and Maintenance is also referred to hereinafter as "O&M".

GENERAL REQUIREMENTS FOR O & M

As part of his undertaking in accordance with the Contract the Contractor shall operate and maintain the Project, as a whole, to achieve the quantity and quality of product water as specified and in accordance with all requirements of the contract.

The operation and maintenance shall include and cover the whole Project.

Acceptance Test

The Contractor shall submit a fully detailed program for the Acceptance Test.

The "Acceptance Test" of the plant as a whole shall be performed under the supervision of the MWC Engineer and in accordance with his instructions. The "Acceptance Test" shall be considered successful when all the units comprising the plant operate to the satisfaction of the MWC Engineer, in accordance with the requirements of the Contract and the instructions contained therein.

The following shall be examined:

- Quality of water under conditions simulating maximum daily loads.

- Adequacy of equipment operation, and effluent and treatment process.

The adequacy of all systems, including control system, pumps, Chemical Treatment Unit, chemical dosing and other systems, shall be tested. Water quality, and the development of environmental nuisances, including odours, shall also be examined.

Test Prior to Taking Over

The Contractor shall submit a program detailing the testing procedures of the plant and all its components, for the approval of the MWC Engineer, hereinafter referred to as "Test Prior to Taking Over".

Comprehensive tests shall be carried out 2 months before the end of the operation and maintenance period, aimed at examining the adequacy of all units involved in the process as well as all equipment, structures, buildings, electrical installations and civil engineering works.  Each item shall be tested separately, and its adequacy tested in the framework of the plant as a whole.

Where the "Test Prior to Taking Over" reveals faults stemming from deficiencies, poor maintenance or other reasons, the Contractor shall replace or repair the faulty items at his expense.

The Contractor shall repair at his expense all the deficiencies and malfunctions pointed out by the Engineer within 30 days from the date of notice. Should the Contractor not comply with the above, the MWC Employer shall perform the necessary repairs at the Contractor’s expense.

Before completing the test, the Contractor shall replenish all stocks of spares kept at the Site, and as stated in the O&M manual.

Prior to Taking-Over, the Contractor shall examine the mechanical condition, including strength, noise, vibration, lubrication, corrosion protection and shall repair any malfunction, abnormality, replacement of bearings, etc. as necessary to prove to the MWC’s Engineer's satisfaction that the Plant is in an acceptable state. The MWC Engineer may carry out any further inspection of the works for purposes of Taking-Over.

On termination, the MWC Engineer will issue a certificate, certifying therein that all defects have been remedied and that Tests Prior to Taking-Over have been satisfactorily completed, also that stocks of spare parts have been replenished.

The Contractor shall prepare a detailed program (referred to as O & M Manual) covering the operation and maintenance of the treatment plants as a whole.  This program shall include the work and activities described in this Chapter, as relevant to the specific items and technology. Notwithstanding the program submitted and approved, the Contractor is deemed to have tendered for and covered in his price, the responsibility for operating and maintaining the treatment plant for the full period of the contract, thereafter handing it over as specified.

The O&M Manual shall include, in elaborate detail, all operating and maintenance procedures and activities which are required, advisable and/or necessary for the plant to achieve full compliance with the contract requirements.

The O&M Manual shall include inter alia full explanations of all plant procedures and processes.

The aforementioned detailed program shall be submitted to the MWC Engineer for his and the Employer's approval within a period of 2 months from the Commencement Date of the O&M Contract.

The MWC Engineer will check the program and will return it to the Contractor within 30 days of receipt with his approval or comments and requirements for changes (if any). The Contractor shall make the requested corrections or changes and resubmit the full program within a further period of 30 days after receiving the MWC’s Engineer's comments. This procedure will be repeated until final approval.

The MWC’s Engineer reserves the right to call for revisions to the last submission, if in his or the Employer's opinion, some significant point or activity has been overlooked.

At least three full copies of the approved O&M Manual shall be submitted to the employer.

During these tests, the Contractor shall revise the O&M Manual to reflect any updates, changes or revisions it deems appropriate based inter alia on its experience, and as necessary to reflect any modifications or adjustments to the plant.

As stated above, the Contractor shall in the framework of this Contract, assume responsibility for operation and maintenance of the plant throughout the contract period including all days, nights, week-ends and holidays.

The Contractor shall be responsible for guarding, fire prevention safety, etc. Any damage caused by fire, accidents, theft etc. shall be reinstated by the Contractor at his own expense.

The Contractor shall safeguard the plant from breaking, theft, breakage, damage and deterioration of any part of the plant.

The Contractor shall keep the As-Built documents and the O&M Manual up to date and in full conformity with all plant components currently in service.

During the O&M period, the Contractor shall promptly notify the MWC in writing of any revisions, modifications or alterations which he, in his professional opinion, believes should be made to the O&M Manual whether as a result of his additional experience in the operation and/or maintenance of the plant. Changes in the Influent quality or volume, changes or modifications of equipment or for any other reason. Such notification shall set forth in detail the proposed revision and the reason therefore. Any such proposed revision shall be subject to the approval of the MWC.

The Contractor shall define, create, purchase and maintain a stock of spare parts and equipment necessary to comply, and ensure future compliance with the Operation and Maintenance Manual and O&M requirements.

The Contractor shall comply fully with all the terms and provisions contained in the O&M Manual.

The MWC shall have the right to perform any testing, sampling, analyses, inspection, evaluation of process or other procedure as and when it deems appropriate, to ensure that the Operation and Maintenance Standards are being complied with by the Contractor, or for any other reason which may seem appropriate. The Contractor shall cooperate with, and assist the MWC with respect to, all such procedures in any way which may be requested by the MWC.

All such inspections, testing, sampling and analyses shall be performed at the expense of the MWC; provided however that the cost of any of the above procedures which indicated the Contractor's non-compliance with its Contractor's Obligations shall be charged to the Contractor.

The Contractor shall employ sufficient staff, having expertise and training as required by applicable Law, the O&M Manual and as necessary or appropriate for full compliance with the Operating and Maintenance requirements. The Contractor shall not sub-contract his Operation and Maintenance Obligations, change any sub-contractors or expand the scope of work of any sub-contractor, without the MWC’s prior written approval, which approval may be granted, withheld, or granted upon such terms and conditions as the MWC may deem appropriate.

The Contractor shall provide all equipment, supplies and any other items or things which are necessary, desirable or required by applicable Law or the O&M Manual or necessary for the operation, maintenance and repair of the plant in full compliance with the Contractor's Operation and Maintenance Obligations.

The Contractor shall provide, inter alia, personnel, water, oil, auxiliary materials and other items that might be required for proper operation and maintenance of the plant and Project as a whole.

The works for operation shall include but shall not be limited to the following activities:

- Operating the treatment plant to achieve the product water qualities as specified

- Maintenance of cleanliness in the plant, and equipment.

- Assurance of proper operation of all units.

- Registration in the plant log of all meter readings and special events.

- Preventive maintenance of the entire treatment plant and other associated works.

Testing of Raw water, and Product water quality by means of the instruments in a plant laboratory approved by MWC. Work shall include sampling, samples handling, transportation to a laboratory approved by the authorities and payment for the tests performed at this laboratory, if required. The tests and results shall be recorded in the laboratory register.

  - Performance Standards

The Contractor shall achieve and maintain the Required Service Levels stipulated in Tables below till completion of O&M. The service level requirements shall be the minimum key performance indicators measured every month for making pro rata payment to the contractor during the O&M period and all the KPIs shall be measured from the date next to the date of issue of certificate of commissioning certificate on completion of Design Build Services and that is the date of commencement of O&M services (Date of O&M). The Contractor shall adhere to the specifications as provided in the Contract. For poor performances below the minimum performance standards will attract penalties. Minimum performance standards to be maintained will be measured based on following Key Performance Indicators:

•	Water Quantity Supplied

•	Water Quality Supplied

•	Power Consumption

The following table provides details of breakup of O&M payment to the contractor under fixed and variable pay category.

| Fixed Pay-out | Key Performance Indicators “Variable Pay-out” |  |  |
| --- | --- | --- | --- |
|  | Quantity | Quality WTP | Power consumption |
| 100% | 50% | 50% | Excess energy amount is deducted from the monthly bill |

The following section defines the KPIs and its implementation

| No | Key Performance Indicator | Definition of KPI |
| --- | --- | --- |
| 1 | Quantity of treated water | - Total Quantity of Treated Water to be supplied is 4.5 MLD - Weightage is 50% from Contract Payment of Variable charges100% |
| 2 | Quality of treated water | - All water samples tested in the previous month at WTP to meet quality standards as defined and summarized in the contract and O&M Policy - Weightage is 50% from Contract Payment of Variable Charges 100% |
| 3 | Power consumption | - Maintaining optimum power consumption in the pumping and treatment functions of the water supply scheme - No Weightage. However, Excess energy charges is deducted from the monthly bills |

| KPI During the O & M Period | Frequency |
| --- | --- |
| - Quantity of treated water Product water delivery data will be recorded on a daily basis. Calculation of Penalty for shortfall in water supply is as follows: - If 100% quantity of water is supplied - No penalty is levied - If quantity of water supplied is between 70% to 100% of required supply any day, proportionate (pro-rata) linear penalty shall be applicable. For example, if there is 1% drop in water supply then 1% amount will be penalized. - If quantity of water supplied is below 70% of full supply any day - Zero payment will be made for the quantity component for that day. - If quantity of water supplied is below 70% of full supply consecutively for 3 days - Zero payment will be made for the quantity component for the entire month. | Monthly |

INSTRUCTION MANUALS, “AS MADE” DRAWINGS

The Contractor’s obligations shall include, the provision of three complete sets of instruction manuals, and as a precedent to applying for the Final Certificate, the provision of three sets of "As Made" drawings as hereinafter specified. In the event of the MWC’s Engineer rejecting all or part of the instruction manuals or "As Made" drawings, the Contractor shall amend them to meet the MWC’s requirements. All drawings shall be prepared by Auto CAD.

The instruction manuals shall cover the commissioning, testing, operation and maintenance of the entire Treatment Plant and other associated works. The greatest importance is attached to completeness and clarity of presentation.

It is emphasized that a collection of standard pamphlets of a general nature unaccompanied by drawings and descriptive matters relating to the Plant and other associated works as installed will not be acceptable. In particular, information supplied by sub contractors and manufacturers employed by the Contractor, shall be coordinated into the comprehensive manual. Cross referencing of descriptive matter, drawings and spare part lists must be complete. The manuals shall be in English and shall be bound.

The instruction manuals shall deal with the Treatment Plant and other associated works as a whole and the process in particular and shall give a step-by-step procedure for any operation likely to be carried out daily, weekly, monthly and at longer intervals to ensure trouble free operation.  Where applicable, fault location charts shall be included to facilitate tracing the cause of malfunction or breakdown. A specific chapter shall be dedicated to mechanical and process faults together with repair instructions.

A separate section of the manual shall be devoted to each size and type of equipment and to each system of the Plant and other associated works.  It shall contain a detailed description of its construction and operation and shall include all relevant pamphlets, a list of parts with their catalogue number (where applicable) and procedure for ordering spares.

Electrical control equipment and instrumentation shall be described in operation step-by step giving the complete sequence of operation.

The "As Made" drawings shall cover the Works to the Treatment Plant and other associated works as completed on the Site, incorporating all modifications carried out during manufacture or after testing at the Contractor’s or sub contractor's and manufacturer's works and all modifications carried out in the course of the erection and commissioning and testing of the Plant and other associated works and the construction of the related Civil Engineering Works.  These drawings may be produced by modifying drawings produced for manufacture and/or construction, or may be produced separately.

Each item of Plant and other associated works, such as pumps, valves, motors, etc. shall be shown on detailed general arrangement drawings, clearly marking the position of the component parts.  All parts shall be numbered and the numbers given shall correspond to the spare parts lists, pamphlets and descriptive matter. Comprehensive electrical circuit drawings done by the Contractor shall be provided showing the relation of one electrical item of equipment to another.

In addition, each item of electrical equipment provided by the Contractor shall be provided with a schematic drawing and a wiring drawing.  The schematic drawing shall show the connections in a schematic form enabling the operation to be ascertained, while the wiring drawing shall show the individual components approximately in their individual physical positions, with the electrical connections shown exactly as wired, to enable a particular component or connection to be located on the actual equipment. Every connection shall be numbered and the number given for a particular connection shall be the same on the schematic drawing, on the wiring drawing and as tagged on the actual equipment itself.

The drawings shall be bound in albums of approved size.  One set of the drawings shall be reproducible to enable further prints to be made if required.

TESTING AND ANALYSES DURING O & M

The Contractor shall perform all tests, sampling and analyses as and when required by the operating and Maintenance Manual and as may be necessary or appropriate to ensure full compliance with the requirements of the contract, for Raw water, Product water, and other environmental requirements.

Without limiting the above obligations, the Contractor shall perform all tests, sampling and analyses required in order to obtain the following information.

Daily measurement of:

- flow entering the plant	(m3/d and m3/h)

- flow of treated secondary water	(m3/d and m3/h)

- flow of treated product water	(m3/d and m3/h)

- flow of reject water 	(m3/d and m3/h)

- Faecal coliform MPN/100 mL.

The daily qualities based on samples in the influent and effluent for

- Total Suspended Solids (mg/L)

- Turbidity (NTU)

- BOD (mg/L)

- COD (mg/L)

- Electrical Conductivity	(us/cm)

All equipment and instrumentation required for the execution of all tests shall be provided by the Contractor.

Analyses that cannot be done in the on-site laboratory shall be done in an authorized laboratory, approved by the MWC’s Engineer.

In any case that a parameter has not reached the desired quality, it shall be analysed every day in the days following until the desired quality will be reached.

MINIMUM MAINTENANCE REQUIREMENTS

A description of the minimum requirements of maintenance works to be performed for the principal equipment and structures is detailed below. The maintenance works shall include, inter alia, the following:

- Lubrication and oil change in all moving systems (including supply of oil and lubrication materials), in accordance with the manufacturer's specifications of each unit process separately.

- Checking of all electro-mechanical systems once a week in order to ensure proper working condition.

- Testing the adequacy of all the valves, gates and non-return valves once a month.

- Testing the adequacy of the laboratory equipment.

- Replenishment of the stock of materials and reagents in the laboratory in order to ensure its proper routine operation.

- Dismantling of any faulty unit, and checking of parts such as shafts, gaskets, bearings, etc., in order to examine the possibility of repairing the unit at the plant premises.

- Where a faulty unit cannot be repaired at the plant's premises, it shall be sent for repair or be replaced.

- Monthly inspection by skilled staff of all electro-mechanical equipment and of the structures in order to obtain an evaluation of their condition.

- Examination of the proper working conditions of laboratory equipment.

- Replenishment of spare parts, including maintaining of records of spare parts use and replacement.

MAINTENANCE OF ELECTRICAL SYSTEM

- Maintenance of Electrical Boards

- The works outlined below shall be carried out once every two months:

- Cleaning of dust and removal of obstacles from the area near the board.

- Cleaning of the electromagnetic surfaces and contacts, and their replacement, where necessary.

- Tightening of all bolts, screws, connections and handles, and closure of panels.

- Testing of earthing, overload relay in starters, buzzers, contacts in switches, insulation in transformers.

- The Contractor shall store electrical drawings for the boards in a plastic cover near the board.

- Maintenance of Electrical Motors

The works outlined below shall be performed once every three months:

- Cleaning the exposed surfaces of dust and dirt.

- Checking of earthing, motor insulation, tightening of connections, motor terminals.

- Maintenance of Cables

The works outlined below shall be performed once every six months:

- Tightening of all connecting bolts on switches and motors, ladders and cables.

- Testing using "Megger".

- Maintenance of Lighting System

The works outlined below shall be performed once every six months:

- Cleaning of lamps and lamp holders, and replacement of burnout bulbs.

- Tightening of all bolts.

MAINTENANCE OF TREATMENT PLANT AND OTHER ASSOCIATED WORKS

All maintenance works required to keep the structures in good condition shall be performed by the Contractor. The following is an outline of some of the additional maintenance works to be performed:

Windows - Windows shall be repaired whenever the need arises. Burglar grilles shall be repainted when necessary.

MAINTENANCE OF DIESEL GENERATOR

- Daily Works

Checking of water in the radiator, diesel gauge, electrical connections, charger connections, general mechanical condition, accumulators and replenishment when necessary.

- Weekly Works

- Manual operation of the generator for a period of 10 minutes without load.

- Testing proper operating conditions of the generator by checking the gauges: frequency, oil pressure, temperature, voltage.

- Cutting off of power from the grid and operation of the Diesel Generator with one of the pumps.

- Thorough inspection of all visible parts for mechanical and electrical defects.

- Tightening of nuts throughout the diesel and water piping systems.

- Cleaning all the electrical parts of dust and dirt.

- Checking water level in the accumulators and replenishment of water, where necessary.

- Monthly Works

- Checking of the fan belt for tightness.

- Checking of the generator water pump to ensure free rotation.

- Checking of the oil tank and connections.

- Checking of the air filter and its replacement, where necessary.

- Checking of the oil filter and connecting pipes, sensors, oil pressure, etc.

- Checking of the diesel generator electrical system, in accordance with instructions.

- Checking of the generator brushes and cleaning them of dirt; replacement of the brushes where broken.

- Maintenance of the Diesel Generator

- Maintenance after 10 hours of operation - checking of oil level, clutch, air purifier, oil filter, radiator water, and cleaning of diesel injectors.

- Maintenance after 50 and 100 hours of operation - oiling of clutch.

- Maintenance after 200 hours of operation.

- Oil change.

- Checking of generator gauges and their recalibration, where necessary.

- Checking of electrolyte (acid concentration) in the accumulators, and performance of appropriate maintenance.

- Maintenance after 6 months.

A specialist shall on behalf of the Contractor check the generator engine in accordance with the manufacturer's instructions, and shall prepare a report on its condition, including all its component parts.

PREVENTIVE MAINTENANCE

Preventive maintenance works shall be carried out by skilled workers, who will visit the plant and associated works to perform periodic inspections of equipment, in addition to works performed by the regular operating personnel.

All preventive maintenance works shall be performed according to the instructions and recommendations of the manufacturers of all the items in the plant and associated works.

The following are minimum requirements for preventive works:

- Periodic painting of all the equipment in the plant.

- Painting of all metal parts, including rust prevention.

- Maintenance of parts in proper working condition.

(a)     Basins, Sumps, Tanks, Pipes, Fittings, Valves, etc.

1.	Weekly Works

- Check for cracks and leakage

- Check levels

- Remove floating matter from the surface of the water

2.	Monthly Works

- Secure flange connections and grease bolts

- Check for leakages in water and air pipes

- Check and clean all filters and replace all damaged parts

- Repair all damaged insulation

3.  	Annual Works

- -	Empty the tanks and remove sediments

- -	Check valve operation every 6 months

- -	Check tank stability and alignment

- -	Open, check, clean and repair non-return valves

- -	Check and adjust automatic accessories, flow control and shut-off devices

- Check and adjust pipe supports and clamps

(b)	Electrical Panel

1.	Monthly Works

- Check panel closure, including bolts and locks

- Clean the panel of external dirt and dust

- Check operation of indicator bulbs

- Check fuse wire for intactness

- Check operation of starters for noise

2.	Semi-Annual Works

- Clean internal panel parts of dirt using compressed air

- Perform visual inspection of insulation

- Check and secure conductors and cables

- Check fuse base for intactness

- Check operation of starters and alignment of protection elements

- Spray all contacts with oil

- Grease axles and moving parts

- Check and touch up painted parts

- Check intactness of connections to earthing bar, doors and cabinet body

- Check earthing conductors

3.	Annual Works

- Check, repair and complete signs

- Check manual and automatic circuit breakers

- Check and calibrate protection devices on automatic circuit breakers

- Tighten busbars

- Check and secure busbar insulation

- Tighten connection of accessories to the panel

- Check resistance of the panel and cables by means of a megommeter and record results

- Check current and power in all lines - record and compare with permissible values

(c)  Pumps

1    Monthly Works

- Check for noise, vibrations and leakages

- Check heating of motor, bearings and mechanical seal

- Perform trial run on standby pump

2.      Semi Annual Works

- Perform backwashing with pressurized water

3.     Annual Works

- Check resistance of motor coils

- Check and calibrate pressure gauges

- Replace oil (according to manufacturer's instructions)

- Record delivery pressure with valve closed

- Check and clean level gauges

- In the event that the above activities will need to be performed at frequencies higher than those indicated, the Contractor shall be responsible for their execution within the required period.

FAILURE REPORTS

The Contractor shall by telephone, with facsimile confirmation immediately report to the Employer of any occurrence that may prevent the proper operation of the plant and associated works and the process or which may cause environmental hazards due to breakdown, such reports shall include but not be limited to the following:

- The Raw water inflow containing chemicals or other pollutants that are considerably in excess of the normal inflow.

- Any major breakdown in the process that may affect the product water, effluent or sludge qualities.

- Any breakdown that may create pollution in the treatment plant area and overflow there from.

PLANT AND ASSOCIATED WORKS OPERATION AND MAINTENANCE REPORT

The Contractor shall prepare an annual report on plant and associated works operation and maintenance, including:

- Monthly and yearly quantities of wastewater, water balance throughout the plant, quantities of effluents, quantities of product water, quantities of reject water, quantities of sludge and sludge cake treated in the various units or removed from the plant.

- Average and ranges per day, month and year of the flow rates.

- Average and ranges per day, month and year of flows, the quality of wastewater, effluents, product water, reject water, recycled flows, overflows, screen, grit, sludge and cake.

- Monthly and yearly consumption of electricity, chemicals, water and fuel for each unit and for the plant as a whole.

- Monthly and yearly loads in each unit, and the efficiency of liquid (both secondary effluent and product water) and sludge treatment from the process point of view.

- Monthly and yearly operating hours of each unit.

- Number of Contractors belonging to the permanent staff of the plant, their functions and period of working during the year.

- Maintenance works performed at the plant or outside, including utilization of spares.

- Vehicles and other permanent or rented facilities of the plant.

- Any special events and data not mentioned above.